## Summary
Building Number | Number of Lighting Fixtures | Number of Compliant Fixtures | Number of Non-Compliant Fixtures | Unknown Compliance | This page updates automatically!!! Do not modify!
Grand Totals | 67 | 17 | 42 | 8
1013 | 0 | 0 | 0 | 0
1018 | 3 | 0 | 3 | 0
1019 | 3 | 0 | 3 | 0
1020 | 3 | 0 | 3 | 0
1021 | 3 | 0 | 3 | 0
1022 | 3 | 0 | 3 | 0
1023 | 3 | 3 | 0 | 0
1098 | 17 | 2 | 15 | 0
1133 | 3 | 0 | 3 | 0
1134 | 7 | 7 | 0 | 0
1352 | 2 | 1 | 1 | 0
1354 | 1 | 0 | 1 | 0
1469 | 15 | 3 | 4 | 8
1555 | 0 | 0 | 0 | 0
1793 | 4 | 1 | 3 | 0

## Template
Building Type:
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes

## 1013
|  |  | Building Type: | Maintenance - pump house
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes

## 1018
|  | 1018 | Building Type: | Restroom
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Recommendation
|  | 1 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required
|  | 2 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required
|  | 3 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required

## 1019
|  | 1019 | Building Type: | Restroom
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Recommendation
|  | 1 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required
|  | 2 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required
|  | 3 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required

## 1020
|  | 1020 | Building Type: | Restroom
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Recommendation
|  | 1 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required
|  | 2 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required
|  | 3 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required

## 1021
|  | 1021 | Building Type: | Restroom
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Recommendation
|  | 1 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required
|  | 2 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required
|  | 3 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Abandon in place | Retrofitted May 2020-field verification required

## 1022
|  | 1022 | Building Type: | Restroom
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Recommendation
|  | 1 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Replace bulb | non-shielded par 16 bulb
|  | 2 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Replace bulb | non-shielded par 16 bulb
|  | 3 | Wall Lantern |  | N | 15W | CF | Entry | N | Archive specifications DieLux similar to Prescolite WB-24 ca 1958. All era comfort stations in this CG have historic Crouse-hinds ca.1958-9: Replace bulb | non-shielded par 16 bulb

## 1023
|  | 1023 | Building Type: | Restroom
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes
|  | 1 | Wall Pack |  | Y | Historically 100W | Mercury | Entry | Y | Modern; No Historic Lighting
|  | 2 | Wall Pack |  | Y | Historically 100W | Mercury | Entry | Y | Modern; No Historic Lighting
|  | 3 | Wall Pack |  | Y | Historically 100W | Mercury | Entry | Y | Modern; No Historic Lighting
This building was rehabbed in 2011; the building dates to 1958. Lighting replacement may have occurred without compliance consideration.

## 1098
|  |  | Building Type: | Park Services - Visitor Center
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Rec
|  | 1 | Double Flood |  | N |  | PAR | General, Security, Walk Way | N |  | Tilt down- PAR 30 Bulbs
|  | 2 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 3 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 4 | Wall Lantern |  | N |  |  | Walk Way | Y |  | Leave empty or use PAR 16 bulb
|  | 5 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 6 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 7 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 8 | Wall Lantern, No Lamp |  | N |  |  | Walk Way | Y | Historic | fixture missing, leave empty or if possible find globe to match and install PAR 30 Amber LED bulb
|  | 9 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 10 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 11 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 12 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 13 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 14 | Wall Lantern |  | N |  |  | Walk Way | N | Historic | PAR 30 bulb replacement
|  | 15 | Wall Lantern |  | N |  |  | Entry | N | Historic | PAR 30 bulb replacement
|  | 16 | Wall Lantern |  | N |  |  | Entry | N | Historic | PAR 30 bulb replacement
|  | 17 | Wall Lantern |  | N |  |  | Entry | N | Historic | PAR 30 bulb replacement

## 1133
|  | 1133 | Building Type: | Restroom
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Recommendation
|  | 1 | Wall Lantern |  | N |  |  | Entry | N | Historic Prescolite Model CF series fixture ca. 1967: See ETIC 117-3638 for original design specs. Abandon in Place | Shielded PAR16 Amber LED bulb
|  | 2 | Bare Bulb |  | N |  | Incandescent | Walk Way | N | Per MT SHPO 10.26.2017 Retain. replace lightbulb. As appropriate, replace globe | PAR 16 shielded amber LED
|  | 3 | Bare Bulb |  | N | 15W | CF | Entry, Walk Way | N | Per MT SHPO 10.26.2017 Retain. Replace lightbulb. As appropriate, replace globe | PAR 16 shielded amber LED

## 1134
|  | 1134 | Building Type: | Restroom
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Rec
|  | 1 | Wall Pack |  | Y |  | Mercury | Entry | Y |  | compliant, no change
|  | 2 | Wall Pack |  | Y |  | Mercury | Walk Way, Security | Y |  | compliant, no change
|  | 3 | Wall Pack |  | Y |  | Mercury | Entry | Y |  | compliant, no change
|  | 4 | Wall Pack |  | Y | Historic 100W | Mercury | Entry | Y | Modern; No Historic Lighting | compliant, no change
|  | 5 | Wall Pack |  | Y | Historic 100W | Mercury | Entry | Y | Modern; No Historic Lighting | compliant, no change
|  | 6 | Wall Pack |  | Y | Historic 100W | Mercury | Entry | Y | Modern; No Historic Lighting | compliant, no change
|  | 7 | Wall Pack |  | Y | Historic 100W | Mercury | Entry, Walk Way | Y | Modern; No Historic Lighting | compliant, no change
Historically this building only had 3-fixtures. Removing a fixture is appropriate.

## 1352
|  | 1352 | Building Type: | Park Services - Sewage Lift Station
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Recommendation
|  | 1 | Wall Lantern |  | N | Historically 100W |  | Entry | N | Appears to be historic Prescolite Series CF 1960s era. Replace bulb | Shielded PAR16 Amber LED bulb
|  | 2 | Emergency |  | N | Unknown |  | Emergency | Y | Only used in emergency

## 1354
|  |  | Building Type: | Maintenance - well house
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Rec
|  | 1 | Wall Lantern |  | N |  |  | Entry | N |  | Barron WLZ Wallpack or field confirm use of PAR 16 bulb

## 1469
|  |  | Building Type: | Kiosks have been replaced with new
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Rec
|  | 1 | Ceiling |  | N |  |  | Security, General | N | On at time of inspection | PAR 16 Shielded bulb
|  | 2 | Bare Bulb |  |  |  | F | General |  |  | Remove
|  | 3 | Bare Bulb |  |  |  | F | General |  |  | Disconnect
|  | 4 | Ceiling |  | N |  |  | Security, General | N |  | CLB-LED amber LED ceiling mounted fixture (RAB Designs Canada)
|  | 5 | Bare Bulb |  |  |  | F | General |  |  | Remove
|  | 6 | Bare Bulb |  |  |  | F | General |  |  | Remove
|  | 7 | Ceiling |  | N |  |  | Security, General | N |  | CLB-LED amber LED ceiling mounted fixture (RAB Designs Canada)
|  | 8 | Bare Bulb |  |  |  | F | General |  |  | Remove
|  | 9 | Bare Bulb |  |  |  | F | General |  |  | Remove
|  | 10 | Ceiling |  | N |  |  | Security, General | N |  | CLB-LED amber LED ceiling mounted fixture (RAB Designs Canada)
|  | 11 | Bare Bulb |  |  |  | F | General |  |  | Remove
|  | 12 | Bare Bulb |  |  |  | F | General |  |  | Remove
|  | 13 | Ceiling |  |  |  | CF | Walk Way | Y |  | PAR 16 Shielded bulb
|  | 14 | Ceiling |  |  |  | CF | Walk Way | Y |  | PAR 16 Shielded bulb
|  | 15 | Ceiling |  |  |  | CF | Walk Way | Y |  | PAR 16 Shielded bulb

## 1555
|  |  | Building Type: | Vault Toilet
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes

## 1793
|  |  | Building Type: | Park Services - Kiosk
Picture (Wide) | Picture (Detail) | Light No. | Type of Luminaire | Light Control Mechanism | Shielded? | Wattage | Bulb Type | Purpose / Application | Compliant? | Notes | Rec
|  | 1 | Flood |  | N | 45W | CF PAR | Entry, Task | N | 45° angle | Angle down and PAR 30 AMBER LED Bulb or remove
|  | 2 | Recessed |  | Y |  |  | Entry | Y |  | No change
|  | 3 | Flood |  | N | 45W | CF PAR | Security, Street | N | 45° angle | Angle down and PAR 30 AMBER LED Bulb or remove
|  | 4 | Post |  | N |  |  | Street | N | Next to Kiosk | Additional Shielding and Amber LED Bulb