## Equations
Capstone Information:
Find | Formula | Variables | Values for C
Cross Sectional Inside Pipe Area | A=pi(d/2)^2 | d= inside diameter | Material | C
Cross Sectional Pipe Wall Area | Am=pi(d0/2)^2-pi(d/2)^2 | do= outside diameter | PVC | 150
Weight of empty pipes | W=pAm | p=density of pipe material | Aluminum with Couplers | 120
Weight of liquid in pipes | Wl=plA | p1= density of liquid | Galv. Steel/ Asb. Cement | 140
Outside surface area of pipes | Ao=2pi(do/2) |  | Cast Iron/Old Steel | 100
Inside surface area of pipes | Ai=2pi(d/2)
Water velocity inside a pipe | V=0.408(Q/d^2) | Q=flow rate of water inside the pipe
Minimum pipe diameter | dmin=0.20655(sqrt(Q/P)) | P=design pressure of a pipeline
Pressure loss due to pipe friction | Ploss=4.53*L*((Q/C)^1.852)/(do^4.857)) | C=pipe coefficient ; L=pipe length
Flow rate | Q=AV
Bernoulli's Equation | P1+(1/2*p(V1)^2)+pgh1=P2+(1/2*p(V2)^2)+pgh2+fp
Link: (pressure loss due to pipe) | http://irrigation.wsu.edu/Content/Calculators/General/Pipe-Velocity.php
Link to Plans:
Pipe Connection between reservoir, turbines, aqueduct and nashua river |  | https://www.digitalcommonwealth.org/search/commonwealth:g732dj29w
https://www.digitalcommonwealth.org/search/commonwealth:qj72pb23n
Water Densitites | https://www.engineeringtoolbox.com/water-density-specific-weight-d_595.html
Equations link | https://www.itacanet.org/fluid-mechanics-for-gravity-flow-water-systems-and-pumps/part-5-energy-in-a-perfect-system-the-bernoulli-equation/
Potential Information on Venturi Meter: | https://www.digitalcommonwealth.org/search/commonwealth:g732dj351

## Dimensions
Plan: | Section: | Length (ft): | Plan: | Section: | Radius (ft) | Chord Length (ft) | Angle (degrees) | Area of Half Circle (ft^2): | Area of Square (ft^2): | Total Area (ft^2): | Length of section following cut out(ft)
Pool and Conduits | Conduit from A to B (longest) | 67 | Pool and Conduits | a | 3.5938 | 6.5 | 129.47 | 9.61 | 12.3197 | 21.9297 | 0
Pool and Conduits | Conduit from B to C | 25 | Pool and Conduits | b | 3.8646 | 7 | 129.82 | 11.19 | 28.4375 | 39.6275 | 10
Pool and Conduits | Conduit from C to D | 13 | Pool and Conduits | c | 4.1236 | 7.5 | 130.85 | 12.98 | 37.4218 | 50.4018 | 10
Pool and Conduits | Conduit from D to E | 40 | Pool and Conduits | e | 4.6875 | 8.5 | 130.1 | 16.54 | 54.009 | 70.549 | 10
Pool and Conduits | Conduit from Increaser to A | 21 | Pool and Conduits | d | 4.4062 | 8 | 130.41 | 14.7 | 46 | 60.7 | 10
Pool and Conduits | Steel Increaser | 33 | Pool and Conduits | f | 5 | 9 | 128.32 | 18.19 | 60.093 | 78.283 | 10
Pool and Conduits | Conduit from A to B (second longest) | 57 | Pool and Conduits | g | 5 | 9 | 128.32 | 18.19 | 60.093 | 78.283 | 10
Pool and Conduits | Conduit from A to B (smallest) | 37 | Pool and Conduits | h | 4.4062 | 8 | 130.41 | 14.7 | 43.25 | 57.95 | 10
Pool and Conduits | Conduit from A to B (second smallest) | 47 | Pool and Conduits | k | 4.236 | 8 | 141.57 | 16.59 | 38.0832 | 54.6732 | 10
Pool and Conduits | E to F | 22 | Pool and Conduits | m | 4.1236 | 7.5 | 130.85 | 12.98 | 25.7025 | 38.6825 | 8
Section Through Gate Chambers and Power Station | Venturi Meter | 3 to the center line, 10 total | Pool and Conduits | n | 3.8646 | 7 | 129.82 | 11.19 | 7.8021 | 18.9921 | none?
Section Through Gate Chambers and Power Station | Venturi Meter to center of the valve | 10 | Area of First Hole | 28.2743 | 38.4845
Section Through Gate Chambers and Power Station | Aqueduct pipe | 10 | Ratio First hole | 0.17349 | 0.16667 | AutoCAD Check:
Section Through Gate Chambers and Power Station | Center of valve to T valve | 20 | Second hole | 38.4845 | 38.4845 | Section | Area (in^2) | Area (ft^2) | Picture
Section Through Gate Chambers and Power Station | T valve length | 7 | Ratio Second hole | 0.23614 | 0.16667 | g | 11273.39 | 78.2874
Section Through Gate Chambers and Power Station | T valve height | 6 | Third Hole | 38.4845 | 38.4845 | g |  | 78.2797
Section Through Gate Chambers and Power Station | T valve to hydroelectric valve above | 5 | Ratio Third hole | 0.23614 | 0.16667
Section Through Gate Chambers and Power Station | T valve to hydroelectric valve to the right | 10 (pipe gets smaller),6 constant diameter, verticle line to the valve is 5 | Fourth Hole | 38.4845 | 38.4845
|  |  | Ratio Fourth hole | 0.23614 | 0.16667
|  |  | Fifth Hole | 19.2422 | 38.4845
|  |  | Ratio Fifth hole | 0.11807 | 0.16667
|  |  | Sixth Hole | 0 | 38.4845
|  |  | Ratio Sixth Hole | 0 | 0.16667
|  |  | Total Area | 162.97 | 230.9069
Note on L8: this is the area of all conduits -Sammi Evans

## Calculations
Point | Diameter of Pipe (ft) | Length of Pipe Section (ft) | Area (ft^2) | Velocity (ft/sec) | Flow | [5 empty] | Material | Equivalent Roughness (E) (ft)
Start | [6 empty] | Gallons/day | Gallons/sec | ft^3/sec |  | Brick | 0.001
Brick Inlet (7') | 7 | 111 | 38.4845 | 6.0306 | 232.0841 |  | 600000000 | 1736.1111 | 232.0841 |  | Cast Iron | 0.00085
48" Cast Iron Pipe | 4 | 81 | 12.5664 | 18.4687 | 232.0841 | [5 empty] | Commercial Steel | 0.00015
48" Cast Iron Pipe (First Valve + Aqueduct) | 4 | - | 12.5664 | 9.2343 | 116.0421 |  | Gravitational force (ft/sec^2) | 32.174 |  |  | Concrete | 0.001
48" Cast Iron Pipe (After valve and aqueduct) | 4 | 7 | 12.5664 | 9.2343 | 116.0421
48" to 60" Increaser | 5 | 12 | 19.6349 | 5.91 | 116.0421 |  | Density of Water (40F) (lbs/ft^3) | 62.42
Tee Line | 5 | 0 | 19.6349 | 5.9099 | 116.04
Tee Branch | - | - | - | - | -
60" to 48" Reducer (After Branch) | 4 | 12 | 12.5664 | 9.2342 | 116.04
End 48" Reducer to End of 48" Hyd. Valve | 4 | 16 | 12.5664 | 9.2342 | 116.04
48" Hyd. Valve to beginning of steel increaser (54") | 4.5 | 6.5 | 15.9043 | 7.2961 | 116.04
Steel Increaser (54" to 96") | 8 | 40 | 50.2654 | 2.3085 | 116.04
Concrete Conduit | 10 | 145 | 78.283 | 1.4823 | 116.04
Conduits Under Pool
Conduit No. 2 & 3 |  |  |  |  | Flow out | Flow Continuing | Velocity Out Orifice
Section g | 10 | 10 | 78.283 | 1.2251 | 20.1322 | 95.9078 | 0.71203
Section h | 8.59 | 10 | 57.95 | 1.1821 | 27.4022 | 68.5055 | 0.71203
Section k | 8.35 | 10 | 54.6732 | 0.7518 | 27.4022 | 41.1033 | 0.71203
Section m | 7.02 | 8 | 38.6825 | 0.35419 | 27.4022 | 13.7011 | 0.71203
Section n | 4.92 | 0 | 18.9921 | 8.4178e-16 | 13.7011 | 1.5987e-14 | 0.35602
0
Conduit No. 1 & 4 |  |  |  |  | Flow out | Flow Continuing | Velocity Out Orifice
Section f | 10 | 10 | 78.283 | 1.2353 | 19.34 | 96.7 | 0.68401
Section e | 9.48 | 10 | 70.549 | 1.0965 | 19.34 | 77.36 | 0.68401
Section d | 8.79 | 10 | 60.7 | 0.95585 | 19.34 | 58.02 | 0.68401
Section c | 8.01 | 10 | 50.4018 | 0.76743 | 19.34 | 38.68 | 0.68401
Section b | 7.1 | 10 | 39.6275 | 0.48804 | 19.34 | 19.34 | 0.68401
Section a | 5.28 | 0 | 21.9297 | 0 | 19.34 | 0 | 0.68401
0
Bernoulli's Equation
Description | Pressure 1(lbs/ft^2) | Density (lbs/ft^3) | Velocity 1(ft/sec) | Gravitational Force (ft/sec^2) | Height 1 (ft) | Presure 2 (lbs/ft^2) | Velocity 2 (ft/sec) | Height 2 (ft) | Major Head Loss (lbs*ft/sec^2) | Reynold's Number | Friction Factor f | Minor Head Loss (ft) | Relative Roughness (E) | Length (ft) | Dynamic Viscosity (μ) (40F) | E/D | Loss Coeff. for Pipe Components (K) | Change in Pressure (lbs/ft^2) | Pressure 1 (PSI) | Pressure 2 (PSI)
1st Drop from Upstream | 0 | 62.42 | 0 | 32.174 | 395 | 219850.4249 | 6.03 | 284 | 0.11648 | 82335881.25 | 0.013 | 0.8476 | 0.001 | 111 | 3.2e-05 | 0.00014286 | 1.5 | 1936.1713 | 0 | 1526.7391
48" Cast Iron Pipe | 219850.4249 | 62.42 | 6.03 | 32.174 | 284 | 207321.7597 | 18.4687 | 284 | 1.5028 | 144101917.7322 | 0.014 | 0 | 0.00085 | 81 | 3.2e-05 | 0.0002125 | 0 | 3017.997 | 1526.7391 | 1439.7344
48" Cast Iron Pipe (@ Valve & Aqueduct) | 207321.7597 | 62.42 | 9.2343 | 32.174 | 284 | 206922.5537 | 9.2343 | 284 | 0 | 72050958.8661 | 0.0135 | 0.19878 | 0.00085 | 0 | 3.2e-05 | 0.0002125 | 0.15 | 399.2059 | 1439.7344 | 1436.9622
48" Cast Iron Pipe (After valve and aqueduct) | 206922.5537 | 62.42 | 9.23 | 32.174 | 284 | 206859.7379 | 9.23 | 284 | 0.031278 | 72017075 | 0.0135 | 0 | 0.00085 | 7 | 3.2e-05 | 0.0002125 | 0 | 62.8158 | 1436.9622 | 1436.526
48" to 60" Increaser | 206859.7379 | 62.42 | 9.23 | 32.174 | 284 | 208394.2372 | 5.91 | 284 | 0.017066 | 57640767.0929 | 0.0131 | 0 | 0.00085 | 12 | 3.2e-05 | 0.00017 | 0 | 34.2727 | 1436.526 | 1447.1822
Tee Line | 208394.2372 | 62.42 | 5.9099 | 32.174 | 284 | 207413.1838 | 5.9099 | 284 | 0 | 57639736.5665 | 0.0131 | 0.4885 | 0 | 0 | 3.2e-05 | 0.00017 | 0.9 | 981.0535 | 1447.1822 | 1440.3693
60" to 48" Reducer | 207413.1838 | 62.42 | 5.9099 | 32.174 | 284 | 205734.1836 | 9.2342 | 284 | 0.053668 | 72049670.7081 | 0.0135 | 0 | 0.00085 | 12 | 3.2e-05 | 0.0002125 | 0 | 107.7818 | 1440.3693 | 1428.7096
End 48" Reducer to End of 48" Hyd. Valve | 205734.1836 | 62.42 | 9.2342 | 32.174 | 284 | 205191.2829 | 9.2342 | 284 | 0.071557 | 72049670.7081 | 0.0135 | 0.19877 | 0.00085 | 16 | 3.2e-05 | 0.0002125 | 0.15 | 542.9007 | 1428.7096 | 1424.9395
48" Hyd. Valve to beginning of steel increaser (54") | 205191.2829 | 62.42 | 9.2342 | 32.174 | 284 | 206159.2203 | 7.2961 | 284 | 0.015893 | 64044151.7406 | 0.0133 | 0 | 0.00085 | 6.5 | 3.2e-05 | 0.00018889 | 0 | 31.9178 | 1424.9395 | 1431.6613
Steel Increaser (54" to 96") | 206159.2203 | 62.42 | 7.2961 | 32.174 | 284 | 218692.9 | 2.3085 | 278.5 | 0.0035199 | 36024835.3541 | 0.0085 | 0 | 0.00015 | 40 | 3.2e-05 | 1.875e-05 | 0 | 7.069 | 1431.6613 | 1518.7007
Concrete Conduit | 218692.9 | 62.42 | 2.3085 | 32.174 | 278.5 | 222795.3234 | 1.4823 | 276.5 | 0.0059415 | 28914390.7362 | 0.012 | 0 | 0.001 | 145 | 3.2e-05 | 0.0001 | 0 | 11.9323 | 1518.7007 | 1547.1897
Conduits 2 & 3 Under Pool
Section g | 222795.3234 | 62.42 | 1.4823 | 32.174 | 276.5 | 222769.647 | 1.2251 | 276.5 | 0.00027991 | 23897918.1265 | 0.012 | 0.023326 | 0.001 | 10 | 3.2e-05 | 0.0001 | 1 | 47.4075 | 1547.1897 | 1547.0114
Section h | 222769.647 | 62.42 | 1.2251 | 32.174 | 276.5 | 221362.9926 | 1.1821 | 277.18 | 0.00031097 | 19807935.6898 | 0.0123 | 0.021717 | 0.001 | 10 | 3.2e-05 | 0.00011641 | 1 | 44.2398 | 1547.0114 | 1537.243
Section k | 221362.9926 | 62.42 | 1.1821 | 32.174 | 277.18 | 220065.6722 | 0.7518 | 277.83 | 0.00012939 | 12245110.9903 | 0.0123 | 0.0087835 | 0.001 | 10 | 3.2e-05 | 0.00011976 | 1 | 17.8999 | 1537.243 | 1528.2338
Section m | 220065.6722 | 62.42 | 0.7518 | 32.174 | 277.83 | 217846.2097 | 0.35419 | 278.94 | 2.8661e-05 | 4850115.3484 | 0.0129 | 0.0019496 | 0.001 | 8 | 3.2e-05 | 0.00014245 | 1 | 3.973 | 1528.2338 | 1512.8209
Section n | 217846.2097 | 62.42 | 0.35419 | 32.174 | 278.94 | 217850.1251 | 8.4178e-16 | 278.94 | 0 | 8.0787e-09 | 0 | 1.1012e-32 | 0.001 | 0 | 3.2e-05 | 0.00020325 | 1 | 2.2115e-29 | 1512.8209 | 1512.8481
Conduits 1 & 4 Under Pool
Section f | 222795.3234 | 62.42 | 1.4823 | 32.174 | 276.5 | 222768.0834 | 1.2353 | 276.5 | 0.00028455 | 24095325.6135 | 0.012 | 0.023713 | 0.001 | 10 | 3.2e-05 | 0.0001 | 1 | 48.1939 | 1547.1897 | 1547.0006
Section e | 222768.0834 | 62.42 | 1.2353 | 32.174 | 276.5 | 221796.2672 | 1.0965 | 276.97 | 0.00024047 | 20277187.7419 | 0.0122 | 0.018686 | 0.001 | 10 | 3.2e-05 | 0.00010549 | 1 | 38.01 | 1547.0006 | 1540.2519
Section d | 221796.2672 | 62.42 | 1.0965 | 32.174 | 276.97 | 220912.7993 | 0.95585 | 277.4 | 0.00019707 | 16388971.2912 | 0.0122 | 0.014199 | 0.001 | 10 | 3.2e-05 | 0.00011377 | 1 | 28.9107 | 1540.2519 | 1534.1167
Section c | 220912.7993 | 62.42 | 0.95585 | 32.174 | 277.4 | 220040.7001 | 0.76743 | 277.83 | 0.00014055 | 11990748.3902 | 0.0123 | 0.0091526 | 0.001 | 10 | 3.2e-05 | 0.00012484 | 1 | 18.6635 | 1534.1167 | 1528.0604
Section b | 220040.7001 | 62.42 | 0.76743 | 32.174 | 277.83 | 220044.0785 | 0.48804 | 277.83 | 6.7254e-05 | 6759147.5932 | 0.0129 | 0.0037016 | 0.001 | 10 | 3.2e-05 | 0.00014085 | 1 | 7.5689 | 1528.0604 | 1528.0839
Section a | 220044.0785 | 62.42 | 0.48804 | 32.174 | 277.83 | 220051.5123 | 0 | 277.83 | 0 | 0 | 0 | 0 | 0.001 | 0 | 3.2e-05 | 0.00018939 | 1 | 0 | 1528.0839 | 1528.1355
Safety Factors for Pipes
Formula | P = 2ST / (OD)(SF)
| 48" Cast Iron Pipe | Steel Increaser at (54") | Steel Increaser at (96")
Ultimate Tensile Strength (S) (psi) | 29007 | 60900 | 60900
Pipe Wall Thickness (T) (in) | 2 | 2 | 2
Fluid Pressure (P) (psi) | 1526.7391 | 1431.6613 | 1518.7007
Pipe Outside Diameter (OD) (in) | 50 | 54 | 96
Safety Factor (SF) | 1.5199 | 3.151 | 1.6708
Note on F5: Flow get's halved due to the aqueduct -Kevin Sifuentes
Note on M5: Ranges from 0.001-0.01 -Kevin Sifuentes
Note on A9: Assuming the hydraulic valve to turbine is closed -Kevin Sifuentes
Note on B14: Equivalent as if it was a pipe -Kevin Sifuentes
Note on B17: Equivalent pipe diameter -Kevin Sifuentes
Note on F17: Ask Professor Marrone (Flow out fountain holes) -Kevin Sifuentes
Note on R34: Assumed 90 Flanged elbow -Kevin Sifuentes
Note on K35: This number goes over the Re values on the Moody Chart -Kevin Sifuentes
Note on R36: Assume (Gate, fully open valve) -Kevin Sifuentes
Note on R41: Assume (Gate, fully open valve) -Kevin Sifuentes