## PVWATTS Inputs
Residential Modules |  |  | Commercial Modules |  |  | Municipal Modules
Parameter | Value | Explanation | Parameter | Value | Explanation | Parameter | Value | Explanation
rated power | 0.2415 | 1 kW/m2 * area * efficency | rated power | 0.294 | 1 kW/m2 * area * efficency (area estimation in calculations) | rated power | 0.3 | 1 kW/m2 * area * efficency
Module Type: Standard |  |  | Module Type: Standard |  |  | Module Type: Standard
cell type | crystalline silicon |  | cell type | crystalline silicon |  | cell type | crystalline silicon
nominal efficiency | 0.15 |  | nominal efficiency | 0.15 |  | nominal efficiency | 0.15
module cover | glass |  | module cover | glass |  | module cover | glass
temperature coefficient | 0.0047 | loss per °C | temperature coefficient | 0.0047 | loss per °C | temperature coefficient | 0.0047 | loss per °C
array type | fixed, roof mount |  | array type | fixed, roof mount |  | array type | fixed, roof mount
System Losses |  |  | System Losses |  |  | System Losses
soiling | 0.03 | light rainfall | soiling | 0.03 | litght rainfall | soiling | 0.03 | light rainfall
shading | 0.02 | little shading | shading | 0.02 | little shading | shading | 0.02 | little shading
snow | 0 | none | snow | 0 | none | snow | 0 | none
mismatch | 0.02 | default | mismatch | 0.02 | default | mismatch | 0.02 | default
wiring | 0.02 | default | wiring | 0.02 | default | wiring | 0.02 | default
connections | 0.005 | default | connections | 0.005 | default | connections | 0.005 | default
light-induced degradation | 0.015 | default | light-induced degradation | 0.015 | default | light-induced degradation | 0.015 | default
nameplate rating | 0.01 | default | nameplate rating | 0.01 | default | nameplate rating | 0.01 | default
age | 0.025 | estimating .005/yr | age | 0.025 | estimating .005/yr | age | 0.025 | estimating .005/yr (source: Gilbert M. Masters Renewable and Efficient Electric Power Systems)
availability | 0.03 | default | availability | 0.03 | default | availability | 0.03 | default
estimated cumulative | 0.1622 | apparently not quite a summation | estimated cumulative | 0.1622 | apparently not quite a summation | estimated cumulative | 0.1622 | apparently not quite a summation
tilt angle (°) | 20 | default | tilt angle (°) | 20 | default | tilt angle (°) | 20 | default
azimuth angle (°) | 180 | facing south | azimuth angle (°) | 180 | facing south | azimuth angle (°) | 180 | facing south
Advanced Parameters |  |  | Advanced Parameters |  |  | Advanced Parameters
DC to AC ratio | 1.2 | inverter power rating, default | DC to AC ratio | 1.2 | inverter power rating, default | DC to AC ratio | 1.2 | inverter power rating, default
inverter efficiency | 0.96 | default | inverter efficiency | 0.96 | default | inverter efficiency | 0.96 | default
ground coverage ratio | n/a | applies only to tracking arrays | ground coverage ratio | n/a | applies only to tracking arrays | ground coverage ratio | n/a | applies only to tracking arrays
Result | 372 | kWh/module/year | Result | 453 | kWh/module/year | Result | 462 | kWh/module/year

## residential
PVWatts: Monthly PV Performance Data
Requested Location: | Eilat, Israel
Location: | EILAT, ISRAEL
Lat (deg N): | 29.55
Long (deg E): | 34.95
Elev (m): | 12
DC System Size (kW): | 0.2415 |  | DC rating 7735 modules
Module Type: | Standard |  | 1.868 MW
Array Type: | Fixed (roof mount)
Array Tilt (deg): | 20
Array Azimuth (deg): | 180
System Losses: | 16.22
Invert Efficiency: | 96
DC to AC Size Ratio: | 1.2
Average Cost of Electricity Purchased from Utility ($/kWh): | No utility data available
Capacity Factor (%) | 17.6
Month | Solar Radiation (kWh/m^2/day) | Plane of Array Irradiance (W/m^2) | DC array Output (kWh) | 7735 modules | AC System Output(kWh) | 7735 modules
1 | 4.4784 | 138.8299 | 26.7153 | 206643.0785 | 25.6219 | 198185.2828
2 | 5.392 | 150.9766 | 28.4467 | 220035.1146 | 27.2893 | 211082.9787
3 | 6.079 | 188.4479 | 34.9632 | 270439.995 | 33.5537 | 259537.6886
4 | 6.5262 | 195.7849 | 35.9356 | 277962.1633 | 34.4533 | 266496.5448
5 | 6.5789 | 203.947 | 36.7497 | 284259.2141 | 35.2328 | 272525.6159
6 | 6.8109 | 204.3275 | 35.9443 | 278029.3205 | 34.4799 | 266701.7932
7 | 6.8256 | 211.5926 | 36.3772 | 281377.3258 | 34.8881 | 269859.3329
8 | 7.1885 | 222.8427 | 38.9051 | 300930.6376 | 37.3207 | 288675.3613
9 | 6.7875 | 203.6251 | 35.9574 | 278130.3513 | 34.5072 | 266913.0316
10 | 5.4356 | 168.5044 | 30.3495 | 234753.4613 | 29.1094 | 225161.2959
11 | 4.1488 | 124.4626 | 23.4415 | 181320.0003 | 22.4623 | 173745.8855
12 | 4.0698 | 126.1623 | 24.301 | 187968.4756 | 23.2867 | 180122.6633
Total | 70.3211 | 2139.5034 | 388.0865 | 3001849.1378 | 372.2052 | 2879007.4745

## commercial
PVWatts: Monthly PV Performance Data
Requested Location: | Eilat, Israel
Location: | EILAT, ISRAEL
Lat (deg N): | 29.55
Long (deg E): | 34.95
Elev (m): | 12
DC System Size (kW): | 0.294 |  | DC rating 12008 modules
Module Type: | Standard |  | 3.530 MW
Array Type: | Fixed (roof mount)
Array Tilt (deg): | 20
Array Azimuth (deg): | 180
System Losses: | 16.22
Invert Efficiency: | 96
DC to AC Size Ratio: | 1.2
Average Cost of Electricity Purchased from Utility ($/kWh): | No utility data available
Capacity Factor (%) | 17.6
Month | Solar Radiation (kWh/m^2/day) | Plane of Array Irradiance (W/m^2) | DC array Output (kWh) | 12008 modules | AC System Output(kWh) | 12008 modules
1 | 4.4784 | 138.8299 | 32.523 | 390536.2613 | 31.1919 | 374551.9947
2 | 5.392 | 150.9766 | 34.6308 | 415846.1684 | 33.2218 | 398927.1664
3 | 6.079 | 188.4479 | 42.5638 | 511106.6699 | 40.8479 | 490501.7711
4 | 6.5262 | 195.7849 | 43.7477 | 525322.6533 | 41.9432 | 503653.5233
5 | 6.5789 | 203.947 | 44.7388 | 537223.4194 | 42.8921 | 515048.398
6 | 6.8109 | 204.3275 | 43.7583 | 525449.5384 | 41.9755 | 504041.8281
7 | 6.8256 | 211.5926 | 44.2852 | 531776.935 | 42.4724 | 510009.0911
8 | 7.1885 | 222.8427 | 47.3627 | 568731.0895 | 45.4338 | 545569.388
9 | 6.7875 | 203.6251 | 43.7742 | 525640.5073 | 42.0087 | 504440.8519
10 | 5.4356 | 168.5044 | 36.9472 | 443662.3076 | 35.4375 | 425533.9122
11 | 4.1488 | 124.4626 | 28.5375 | 342677.9839 | 27.3454 | 328363.5156
12 | 4.0698 | 126.1623 | 29.5839 | 355243.0414 | 28.349 | 340415.0322
Total | 70.3211 | 2139.5034 | 472.4531 | 5673216.5754 | 453.1193 | 5441056.4727

## municipal
PVWatts: Monthly PV Performance Data
Requested Location: | Eilat, Israel
Location: | EILAT, ISRAEL
Lat (deg N): | 29.55
Long (deg E): | 34.95
Elev (m): | 12
DC System Size (kW): | 0.3 |  | DC rating 4383 modules
Module Type: | Standard |  | 1.315 MW
Array Type: | Fixed (roof mount)
Array Tilt (deg): | 20
Array Azimuth (deg): | 180
System Losses: | 16.22
Invert Efficiency: | 96
DC to AC Size Ratio: | 1.2
Average Cost of Electricity Purchased from Utility ($/kWh): | No utility data available
Capacity Factor (%) | 17.6
Month | Solar Radiation (kWh/m^2/day) | Plane of Array Irradiance (W/m^2) | DC array Output (kWh) | 4383 modules | AC System Output(kWh) | 4383 modules
1 | 4.4784 | 138.8299 | 33.1867 | 145457.5187 | 31.8284 | 139504.0596
2 | 5.392 | 150.9766 | 35.3375 | 154884.2692 | 33.8998 | 148582.7537
3 | 6.079 | 188.4479 | 43.4325 | 190364.6094 | 41.6816 | 182690.3466
4 | 6.5262 | 195.7849 | 44.6405 | 195659.525 | 42.7991 | 187588.6514
5 | 6.5789 | 203.947 | 45.6518 | 200091.8986 | 43.7674 | 191832.6763
6 | 6.8109 | 204.3275 | 44.6513 | 195706.8086 | 42.8322 | 187733.3614
7 | 6.8256 | 211.5926 | 45.189 | 198063.3667 | 43.3392 | 189955.8432
8 | 7.1885 | 222.8427 | 48.3293 | 211827.1209 | 46.3611 | 203200.5642
9 | 6.7875 | 203.6251 | 44.6676 | 195777.9347 | 42.8661 | 187882.0341
10 | 5.4356 | 168.5044 | 37.7013 | 165244.6543 | 36.1608 | 158492.6233
11 | 4.1488 | 124.4626 | 29.1199 | 127632.4705 | 27.9035 | 122300.8716
12 | 4.0698 | 126.1623 | 30.1876 | 132312.3893 | 28.9276 | 126789.6161
Total | 70.3211 | 2139.5034 | 482.095 | 2113022.5659 | 462.3667 | 2026553.4016

## total
month | Solar Radiation (kWh/m^2/day) | Plane of Array Irradiance (W/m^2) | DC array Output (kWh) | AC system output (kWh) | MWh
1 | 4.4784 | 138.8299 | 742636.8585 | 712241.3371 | 712.2413 |  |  | Residential | Commercial | Municipal | Total (GWh)
2 | 5.392 | 150.9766 | 790765.5522 | 758592.8988 | 758.5929 |  |  | 2.879 | 5.4411 | 2.0266 | 10.3466
3 | 6.079 | 188.4479 | 971911.2742 | 932729.8063 | 932.7298
4 | 6.5262 | 195.7849 | 998944.3416 | 957738.7194 | 957.7387 | total DC rating
5 | 6.5789 | 203.947 | 1021574.5321 | 979406.6902 | 979.4067 | 6.7312 MW
6 | 6.8109 | 204.3275 | 999185.6675 | 958476.9828 | 958.477
7 | 6.8256 | 211.5926 | 1011217.6274 | 969824.2673 | 969.8243
8 | 7.1885 | 222.8427 | 1081488.8481 | 1037445.3136 | 1037.4453
9 | 6.7875 | 203.6251 | 999548.7933 | 959235.9176 | 959.2359
10 | 5.4356 | 168.5044 | 843660.4232 | 809187.8315 | 809.1878
11 | 4.1488 | 124.4626 | 651630.4547 | 624410.2727 | 624.4103
12 | 4.0698 | 126.1623 | 675523.9064 | 647327.3115 | 647.3273
totals | 70.3211 | 2139.5034 | 10788088.2791 | 10346617.3488 | 10346.6173
|  |  | 10788088.2791 |  |  |  | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec

## hourly
Res ( 7735) | Com (12008) | Mun (4383) | Total (7735*A, 12008*B, 4383*c)
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
44.539 | 54.222 | 55.328 | 1238109.565
90.175 | 109.778 | 112.018 | 2506692.743
120.748 | 146.997 | 149.997 | 3356562.607
136.055 | 165.633 | 169.013 | 3782090.468
133.555 | 162.589 | 165.907 | 3712587.018
121.975 | 148.492 | 151.522 | 3390689.487
98.481 | 119.889 | 122.336 | 2737576.335
63.687 | 77.532 | 79.115 | 1770384.246
26.571 | 32.347 | 33.007 | 738619.142
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
37.389 | 45.517 | 46.446 | 1039344.869
96.002 | 116.872 | 119.257 | 2668677.877
85.296 | 103.839 | 105.958 | 2371077.186
54.659 | 66.542 | 67.9 | 1519429.401
142.139 | 173.039 | 176.57 | 3951203.787
126.226 | 153.666 | 156.802 | 3508842.604
95.696 | 116.5 | 118.877 | 2660178.451
74.638 | 90.863 | 92.718 | 2074790.828
40.387 | 49.167 | 50.17 | 1122685.891
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
59.809 | 72.811 | 74.297 | 1662580.854
96.631 | 117.638 | 120.039 | 2686168.826
126.821 | 154.391 | 157.541 | 3525389.766
133.014 | 161.931 | 165.235 | 3697555.743
134.928 | 164.26 | 167.613 | 3750749.939
124.046 | 151.012 | 154.094 | 3448241.908
96.04 | 116.919 | 119.305 | 2669746.567
78.821 | 95.956 | 97.914 | 2191077.145
32.076 | 39.049 | 39.846 | 891653.27
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
7.111 | 8.657 | 8.834 | 197676.263
44.341 | 53.981 | 55.082 | 1232605.889
56.073 | 68.263 | 69.656 | 1558729.007
78.747 | 95.866 | 97.822 | 2189020.799
57.678 | 70.217 | 71.65 | 1603347.016
40.9 | 49.791 | 50.807 | 1136938.909
39.689 | 48.317 | 49.303 | 1103280
36.343 | 44.244 | 45.147 | 1010274.358
9.173 | 11.167 | 11.395 | 254990.776
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
46.92 | 57.12 | 58.286 | 1304290.698
98.023 | 119.332 | 121.767 | 2724851.322
124.996 | 152.17 | 155.275 | 3474671.745
108.077 | 131.572 | 134.257 | 3004340.602
129.628 | 157.808 | 161.029 | 3603421.151
131.429 | 160.001 | 163.266 | 3653490.201
102.564 | 124.861 | 127.409 | 2851097.075
69.795 | 84.968 | 86.702 | 1940174.935
31.487 | 38.333 | 39.115 | 875295.654
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
61.587 | 74.976 | 76.506 | 1712013.051
108.075 | 131.569 | 134.255 | 3004280.342
128.936 | 156.966 | 160.169 | 3584188.415
136.91 | 166.673 | 170.074 | 3805842.576
134.585 | 163.842 | 167.186 | 3741205.949
123.698 | 150.589 | 153.663 | 3438581.671
103.584 | 126.102 | 128.676 | 2879441.964
72.898 | 88.746 | 90.557 | 2026439.329
33.531 | 40.82 | 41.653 | 932093.944
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
56.887 | 69.254 | 70.667 | 1581356.438
105.39 | 128.301 | 130.92 | 2929652.418
135.021 | 164.373 | 167.728 | 3753330.243
144.969 | 176.484 | 180.086 | 4029872.025
141.697 | 172.501 | 176.021 | 3938918.346
129.987 | 158.245 | 161.474 | 3613395.947
108.374 | 131.933 | 134.626 | 3012590.112
75.112 | 91.44 | 93.307 | 2087967.421
32.451 | 39.506 | 40.312 | 902084.029
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
56.047 | 68.232 | 69.624 | 1558015.393
103.343 | 125.808 | 128.376 | 2872732.577
135.482 | 164.934 | 168.3 | 3766139.642
148.343 | 180.591 | 184.277 | 4123655.924
144.685 | 176.138 | 179.733 | 4021973.318
131.751 | 160.392 | 163.665 | 3662424.816
109.869 | 133.754 | 136.484 | 3054164.119
77.267 | 94.064 | 95.983 | 2147874.246
32.053 | 39.021 | 39.817 | 891012.034
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
55.98 | 68.149 | 69.54 | 1556132.312
99.897 | 121.613 | 124.095 | 2776940.584
134.45 | 163.678 | 167.019 | 3737460.451
138.412 | 168.501 | 171.94 | 3847589.848
145.533 | 177.171 | 180.787 | 4045556.544
134.483 | 163.718 | 167.059 | 3738371.346
115.881 | 141.073 | 143.952 | 3221285.735
45.361 | 55.223 | 56.35 | 1260967.169
22.56 | 27.464 | 28.025 | 627122.887
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
58.591 | 71.329 | 72.784 | 1628732.289
104.907 | 127.713 | 130.319 | 2916221.526
137.814 | 167.773 | 171.197 | 3830965.925
149.462 | 181.954 | 185.667 | 4154770.663
146.349 | 178.164 | 181.8 | 4068232.227
134.135 | 163.294 | 166.627 | 3728694.718
112.002 | 136.35 | 139.133 | 3113446.209
70.257 | 85.53 | 87.275 | 1953008.46
30.026 | 36.554 | 37.3 | 834677.442
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
40.009 | 48.706 | 49.7 | 1112166.363
100.74 | 122.64 | 125.143 | 2800386.789
133.313 | 162.294 | 165.606 | 3705853.505
143.398 | 174.572 | 178.134 | 3986205.428
139.409 | 169.715 | 173.179 | 3875309.892
129.897 | 158.136 | 161.363 | 3610904.412
111.413 | 135.634 | 138.402 | 3097088.593
71.808 | 87.418 | 89.202 | 1996122.59
31.172 | 37.948 | 38.723 | 866517.913
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
39.184 | 47.702 | 48.676 | 1089240.764
97.366 | 118.533 | 120.952 | 2706602.89
125.755 | 153.093 | 156.217 | 3495754.78
147.993 | 180.165 | 183.842 | 4113926.661
145.923 | 177.646 | 181.271 | 4056398.366
136.062 | 165.64 | 169.021 | 3782263.733
110.9 | 135.009 | 137.764 | 3082819.184
73.447 | 89.414 | 91.239 | 2041696.394
30.83 | 37.533 | 38.299 | 857030.831
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.726 | 14.275 | 14.567 | 325961.971
22.206 | 27.033 | 27.585 | 617280.729
47.297 | 57.579 | 58.755 | 1314774.092
75.461 | 91.866 | 93.74 | 2097680.183
69.037 | 84.045 | 85.76 | 1919099.635
64.017 | 77.933 | 79.524 | 1779544.651
107.095 | 130.376 | 133.037 | 2977036.004
56.504 | 68.788 | 70.191 | 1570711.897
20.07 | 24.432 | 24.931 | 557893.479
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
20.172 | 24.557 | 25.058 | 560740.09
40.171 | 48.904 | 49.902 | 1116682.383
110.425 | 134.43 | 137.173 | 3069602.074
97.369 | 118.537 | 120.956 | 2706691.659
121.169 | 147.51 | 150.52 | 3368271.455
113.808 | 138.548 | 141.376 | 3163640.272
115.513 | 140.625 | 143.495 | 3211056.64
67.478 | 82.147 | 83.823 | 1875759.715
25.967 | 31.612 | 32.257 | 721834.072
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
30.243 | 36.818 | 37.569 | 840705.076
31.315 | 38.122 | 38.9 | 870489.201
139.533 | 169.867 | 173.333 | 3878769.23
94.186 | 114.661 | 117.001 | 2618193.381
148.718 | 181.047 | 184.742 | 4134070.292
144.57 | 175.998 | 179.59 | 4018775.904
121.592 | 148.025 | 151.045 | 3380028.555
78.223 | 95.229 | 97.172 | 2174469.613
31.736 | 38.635 | 39.423 | 882198.049
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
40.397 | 49.179 | 50.182 | 1122959.933
92.605 | 112.737 | 115.038 | 2574257.125
123.201 | 149.984 | 153.045 | 3424763.842
150.196 | 182.848 | 186.579 | 4175180.601
155.909 | 189.802 | 193.676 | 4333980.439
64.717 | 78.786 | 80.394 | 1799015.185
76.399 | 93.007 | 94.905 | 2123742.936
31.45 | 38.287 | 39.068 | 874251.09
20.742 | 25.251 | 25.766 | 576585.756
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
40.804 | 49.675 | 50.689 | 1134286.227
95.5 | 116.261 | 118.634 | 2654727.41
118.129 | 143.81 | 146.745 | 3283781.63
142.432 | 173.395 | 176.934 | 3959340.402
150.492 | 183.208 | 186.947 | 4183405.985
142.277 | 173.207 | 176.742 | 3955042.437
117.655 | 143.232 | 146.155 | 3270588.646
84.396 | 102.743 | 104.839 | 2346050.341
36.738 | 44.724 | 45.637 | 1021241.193
7.441 | 9.059 | 9.244 | 206853.059
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
49.545 | 60.315 | 61.546 | 1377249.213
99.173 | 120.733 | 123.196 | 2756833.087
133.781 | 162.864 | 166.187 | 3718864.568
144.212 | 175.563 | 179.146 | 4008837.242
140.889 | 171.517 | 175.017 | 3916452.062
132.129 | 160.853 | 164.136 | 3672948.727
112.545 | 137.011 | 139.807 | 3128537.744
81.062 | 98.685 | 100.699 | 2253387.767
37.564 | 45.73 | 46.663 | 1044207.309
6.827 | 8.311 | 8.48 | 189773.173
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
59.994 | 73.036 | 74.527 | 1667721.719
104.92 | 127.729 | 130.335 | 2916584.337
132.249 | 160.999 | 164.285 | 3676283.162
137.59 | 167.501 | 170.919 | 3824748.635
143.994 | 175.297 | 178.875 | 4002769.091
118.089 | 143.76 | 146.694 | 3282648.297
104.697 | 127.457 | 130.058 | 2910379.165
47.427 | 57.737 | 58.916 | 1318382.569
25.623 | 31.193 | 31.83 | 712270.339
5.178 | 6.304 | 6.433 | 143946.101
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
44.367 | 54.012 | 55.114 | 1233319.503
98.949 | 120.46 | 122.918 | 2750603.789
131.137 | 159.646 | 162.904 | 3645382.095
143.022 | 174.113 | 177.667 | 3975738.535
142.216 | 173.132 | 176.665 | 3953332.511
130.291 | 158.615 | 161.852 | 3621847.121
110.227 | 134.189 | 136.928 | 3064102.781
80.298 | 97.754 | 99.749 | 2232134.929
35.535 | 43.259 | 44.142 | 987791.683
6.808 | 8.287 | 8.457 | 189237.207
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
43.495 | 52.951 | 54.031 | 1209087.306
89.088 | 108.454 | 110.668 | 2476469.156
122.291 | 148.876 | 151.914 | 3399462.955
142.564 | 173.556 | 177.098 | 3963013.522
142.813 | 173.859 | 177.407 | 3969932.308
128.394 | 156.306 | 159.496 | 3569121.006
109.494 | 133.297 | 136.018 | 3043733.36
63.587 | 77.41 | 78.99 | 1767597.895
37.977 | 46.233 | 47.177 | 1055694.75
7.572 | 9.219 | 9.407 | 210502.053
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
49.873 | 60.714 | 61.954 | 1386365.749
99.731 | 121.411 | 123.889 | 2772328.06
130.873 | 159.324 | 162.576 | 3638035.855
149.835 | 182.408 | 186.131 | 4165141.162
148.342 | 180.591 | 184.276 | 4123643.806
140.917 | 171.551 | 175.052 | 3917230.319
124.555 | 151.632 | 154.727 | 3462398.422
73.136 | 89.035 | 90.853 | 2033047.939
37.694 | 45.889 | 46.825 | 1047832.177
7.747 | 9.432 | 9.624 | 215364.493
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
56.699 | 69.025 | 70.434 | 1576131.187
104.349 | 127.034 | 129.626 | 2900714.545
137.261 | 167.1 | 170.51 | 3815595.965
147.43 | 179.48 | 183.143 | 4098282.659
145.328 | 176.921 | 180.531 | 4039846.821
137.17 | 166.99 | 170.398 | 3813080.304
116.753 | 142.134 | 145.035 | 3245517.932
83.97 | 102.224 | 104.31 | 2334204.472
39.206 | 47.729 | 48.703 | 1089853.491
7.67 | 9.337 | 9.527 | 213202.987
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
48.444 | 58.975 | 60.179 | 1346650.697
106.991 | 130.251 | 132.909 | 2974169.54
141.63 | 172.419 | 175.938 | 3937051.656
153.354 | 186.692 | 190.502 | 4262960.992
157.449 | 191.677 | 195.588 | 4376787.635
147.688 | 179.794 | 183.463 | 4105451.361
125.952 | 153.332 | 156.462 | 3501222.322
86.625 | 105.457 | 107.609 | 2408022.278
45.022 | 54.81 | 55.928 | 1251536.074
11.464 | 13.957 | 14.241 | 318687.999
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
48.533 | 59.083 | 60.289 | 1349118.106
98.539 | 119.961 | 122.409 | 2739209.5
111.656 | 135.929 | 138.703 | 3103829.841
119.147 | 145.048 | 148.009 | 3312061.876
122.067 | 148.604 | 151.636 | 3393245.665
135.866 | 165.402 | 168.778 | 3776824.7
87.121 | 106.061 | 108.225 | 2421811.598
64.328 | 78.313 | 79.911 | 1788209.497
37.076 | 45.137 | 46.058 | 1030660.17
5.504 | 6.701 | 6.838 | 153010.002
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
5.152 | 6.272 | 6.4 | 143216.096
14.079 | 17.14 | 17.49 | 391376.855
23.159 | 28.193 | 28.768 | 643766.553
43.935 | 53.486 | 54.577 | 1221308.104
68.907 | 83.886 | 85.598 | 1915474.767
41.65 | 50.704 | 51.739 | 1157788.419
30.963 | 37.694 | 38.464 | 860716.069
24.656 | 30.016 | 30.629 | 685393.195
11.396 | 13.873 | 14.156 | 316780.792
1.714 | 2.086 | 2.129 | 47637.885
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
18.094 | 22.028 | 22.477 | 502986.005
95.473 | 116.228 | 118.6 | 2653973.279
135.949 | 165.503 | 168.88 | 3779126.579
153.726 | 187.144 | 190.964 | 4273290.974
157.076 | 191.223 | 195.126 | 4366425.902
143.795 | 175.055 | 178.628 | 3997241.289
124.501 | 151.567 | 154.66 | 3460906.551
84.832 | 103.274 | 105.382 | 2358179.018
38.925 | 47.388 | 48.355 | 1082059.944
10.651 | 12.967 | 13.231 | 296084.694
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
39.062 | 47.554 | 48.524 | 1085853.694
45.175 | 54.996 | 56.118 | 1255785.787
131.95 | 160.635 | 163.913 | 3667969.009
156.19 | 190.144 | 194.025 | 4341790.377
168.331 | 204.925 | 209.107 | 4679295.666
90.894 | 110.653 | 112.911 | 2526675.227
81.559 | 99.29 | 101.316 | 2267201.213
66.656 | 81.147 | 82.803 | 1852922.885
28.51 | 34.707 | 35.416 | 792514.834
6.714 | 8.173 | 8.34 | 186628.394
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
65.141 | 79.302 | 80.921 | 1810800.794
111.958 | 136.296 | 139.078 | 3112216.372
137.463 | 167.346 | 170.762 | 3821216.919
147.694 | 179.801 | 183.471 | 4105616.891
146.675 | 178.561 | 182.205 | 4077296.128
134.899 | 164.225 | 167.576 | 3749943.173
115.475 | 140.579 | 143.448 | 3210004.341
83.786 | 102 | 104.082 | 2329092.116
42.502 | 51.741 | 52.797 | 1181468.149
9.019 | 10.98 | 11.204 | 250716.937
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.565 | 0.688 | 0.702 | 15708.645
54.327 | 66.137 | 67.487 | 1510187.962
105.545 | 128.489 | 131.111 | 2933946
114.826 | 139.788 | 142.641 | 3191948.917
141.629 | 172.417 | 175.936 | 3937011.139
146.784 | 178.693 | 182.34 | 4080316.004
139.151 | 169.401 | 172.858 | 3868136.807
124.598 | 151.684 | 154.78 | 3463587.742
88.019 | 107.154 | 109.34 | 2446769.417
46.264 | 56.322 | 57.471 | 1286062.009
14.645 | 17.829 | 18.193 | 407109.626
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.711 | 14.257 | 14.548 | 325546.525
30.805 | 37.501 | 38.267 | 856312.944
65.636 | 79.905 | 81.535 | 1824561.605
65.4 | 79.618 | 81.243 | 1818010.013
34.045 | 41.446 | 42.292 | 946387.479
56.858 | 69.219 | 70.631 | 1580554.055
63.389 | 77.169 | 78.744 | 1762094.219
36.477 | 44.407 | 45.314 | 1014000.113
23.556 | 28.677 | 29.262 | 654814.422
1.065 | 1.296 | 1.322 | 29594.469
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
59.141 | 71.998 | 73.467 | 1644013.48
109.769 | 133.632 | 136.359 | 3051377.768
133.855 | 162.954 | 166.279 | 3720920.914
146.247 | 178.04 | 181.673 | 4065397.624
156.992 | 191.12 | 195.021 | 4364079.123
136.565 | 166.253 | 169.646 | 3796254.717
114.182 | 139.004 | 141.841 | 3174046.905
82.742 | 100.73 | 102.786 | 2300086.248
42.622 | 51.888 | 52.947 | 1184818.975
6.32 | 7.694 | 7.852 | 175690.068
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
58.925 | 71.735 | 73.199 | 1638009.972
110.673 | 134.733 | 137.482 | 3076513.125
140.772 | 171.375 | 174.873 | 3913210.779
149.78 | 182.34 | 186.062 | 4163596.766
149.949 | 182.547 | 186.272 | 4168310.067
138.546 | 168.664 | 172.106 | 3851311.22
118.137 | 143.819 | 146.754 | 3283991.029
86.416 | 105.202 | 107.349 | 2402204.043
44.601 | 54.297 | 55.405 | 1239827.226
7.287 | 8.871 | 9.052 | 202562.829
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
63.21 | 76.951 | 78.522 | 1757118.884
113.179 | 137.783 | 140.595 | 3146165.714
137.296 | 167.143 | 170.554 | 3816575.886
146.007 | 177.748 | 181.376 | 4058733.137
144.59 | 176.023 | 179.615 | 4019340.379
134.393 | 163.609 | 166.948 | 3735879.811
114.146 | 138.961 | 141.797 | 3173059.249
85.176 | 103.692 | 105.808 | 2367726.36
43.976 | 53.536 | 54.628 | 1222449.172
6.904 | 8.405 | 8.576 | 191918.288
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
65.441 | 79.667 | 81.293 | 1819134.69
114.535 | 139.433 | 142.279 | 3183848.546
138.965 | 169.174 | 172.627 | 3862959.808
149.415 | 181.896 | 185.609 | 4153456.44
147.819 | 179.953 | 183.626 | 4109088.347
138.677 | 168.825 | 172.27 | 3854976.605
121.63 | 148.072 | 151.093 | 3381097.245
78.766 | 95.888 | 97.845 | 2189532.749
44.245 | 53.864 | 54.963 | 1229936.816
12.544 | 15.271 | 15.583 | 348702.297
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
58.272 | 70.94 | 72.388 | 1619858.044
105.985 | 129.026 | 131.659 | 2946199.58
139.973 | 170.402 | 173.879 | 3890990.028
151.309 | 184.202 | 187.961 | 4206105.794
154.005 | 187.484 | 191.311 | 4281052.66
143.282 | 174.43 | 177.99 | 3982971.88
121.014 | 147.321 | 150.328 | 3363961.482
88.505 | 107.745 | 109.944 | 2460272.687
45.443 | 55.322 | 56.451 | 1263232.914
7.639 | 9.299 | 9.489 | 212340.344
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
65.594 | 79.854 | 81.483 | 1823396.411
114.201 | 139.027 | 141.864 | 3174570.863
139.244 | 169.514 | 172.974 | 3870721.494
150.262 | 182.927 | 186.66 | 4176994.766
149.149 | 181.573 | 185.279 | 4146073.956
137.843 | 167.809 | 171.233 | 3831780.316
117.874 | 143.498 | 146.427 | 3276668.915
86.707 | 105.557 | 107.711 | 2410304.414
45.304 | 55.153 | 56.278 | 1259370.138
7.891 | 9.606 | 9.803 | 219352.282
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.377 | 0.459 | 0.469 | 10483.394
59.558 | 72.506 | 73.985 | 1655609.433
106.091 | 129.155 | 131.79 | 2949142.695
133.416 | 162.419 | 165.734 | 3708712.234
144.114 | 175.443 | 179.023 | 4006099.143
148.004 | 180.179 | 183.856 | 4114241.22
138.512 | 168.624 | 172.065 | 3850388.207
118.526 | 144.293 | 147.238 | 3294813.108
85.534 | 104.128 | 106.253 | 2377681.413
36.018 | 43.848 | 44.743 | 1001234.583
10.077 | 12.267 | 12.518 | 280114.125
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.366 | 0.445 | 0.454 | 10164.452
47.538 | 57.872 | 59.053 | 1321462.705
98.949 | 120.459 | 122.918 | 2750591.781
133.886 | 162.992 | 166.319 | 3721792.323
151.53 | 184.471 | 188.236 | 4212250.706
154.794 | 188.445 | 192.291 | 4302990.603
146.984 | 178.937 | 182.589 | 4085884.323
126.224 | 153.663 | 156.799 | 3508777.961
90.756 | 110.485 | 112.74 | 2522840.96
47.463 | 57.781 | 58.961 | 1319386.616
10.448 | 12.719 | 12.979 | 290431.989
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.765 | 0.931 | 0.95 | 21260.573
57.045 | 69.446 | 70.863 | 1585743.172
107.709 | 131.124 | 133.8 | 2994111.507
137.76 | 167.708 | 171.131 | 3829478.437
154.666 | 188.29 | 192.132 | 4299442.386
155.234 | 188.981 | 192.837 | 4315223.409
143.555 | 174.762 | 178.329 | 3990556.028
124.069 | 151.04 | 154.123 | 3448883.144
90.808 | 110.549 | 112.805 | 2524296.587
46.434 | 56.529 | 57.682 | 1290787.428
10.377 | 12.633 | 12.891 | 288464.412
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.788 | 0.96 | 0.979 | 21913.817
56.266 | 68.498 | 69.896 | 1564095.662
95.344 | 116.071 | 118.439 | 2650384.545
144.303 | 175.673 | 179.258 | 4011352.903
157.459 | 191.69 | 195.602 | 4377082.451
159.606 | 194.302 | 198.268 | 4436739.47
147.027 | 178.989 | 182.642 | 4087073.643
114.753 | 139.699 | 142.55 | 3189916.697
90.528 | 110.208 | 112.457 | 2516510.775
44.82 | 54.563 | 55.677 | 1245907.495
14.242 | 17.338 | 17.692 | 395900.61
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.757 | 0.922 | 0.941 | 21051.174
39.124 | 47.629 | 48.601 | 1087571.355
92.183 | 112.223 | 114.513 | 2562519.768
131.31 | 159.856 | 163.118 | 3650179.892
149.689 | 182.229 | 185.948 | 4161060.331
155.116 | 188.837 | 192.69 | 4311937.226
145.496 | 177.125 | 180.74 | 4044511.98
123.324 | 150.133 | 153.197 | 3428170.655
88.924 | 108.255 | 110.465 | 2471921.275
46.807 | 56.982 | 58.145 | 1301141.536
12.868 | 15.665 | 15.985 | 357701.555
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.819 | 0.997 | 1.017 | 22764.452
58.679 | 71.436 | 72.894 | 1631179.955
107.786 | 131.218 | 133.896 | 2996256.622
138.969 | 169.179 | 172.632 | 3863072.703
152.321 | 185.435 | 189.219 | 4234253.292
150.996 | 183.822 | 187.573 | 4197421.095
141.254 | 171.961 | 175.471 | 3926596.771
120.276 | 146.423 | 149.411 | 3343450.657
88.895 | 108.22 | 110.428 | 2471114.509
46.602 | 56.732 | 57.89 | 1295436.196
9.734 | 11.85 | 12.092 | 270586.526
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
2.395 | 2.916 | 2.975 | 66580.078
49.724 | 60.533 | 61.769 | 1382228.931
98.459 | 119.863 | 122.31 | 2736979.999
125.035 | 152.217 | 155.324 | 3475752.553
144.878 | 176.374 | 179.973 | 4027351.981
150.227 | 182.885 | 186.617 | 4176031.236
141.076 | 171.745 | 175.25 | 3921657.57
117.638 | 143.211 | 146.134 | 3270112.94
85.365 | 103.922 | 106.043 | 2372980.12
45.617 | 55.534 | 56.667 | 1268071.228
14.603 | 17.778 | 18.14 | 405940.049
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.544 | 16.488 | 16.825 | 376494.719
65.545 | 79.794 | 81.423 | 1822033.936
112.483 | 136.936 | 139.731 | 3126824.466
141.638 | 172.429 | 175.948 | 3937277.446
150.088 | 182.716 | 186.444 | 4172168.46
150.567 | 183.299 | 187.04 | 4185486.457
142.845 | 173.899 | 177.448 | 3970839.851
121.703 | 148.16 | 151.184 | 3383117.457
90.002 | 109.568 | 111.804 | 2501894.946
47.14 | 57.388 | 58.559 | 1310407.101
10.98 | 13.367 | 13.64 | 305225.356
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.492 | 16.425 | 16.76 | 375051.1
62.245 | 75.777 | 77.323 | 1730302
109.518 | 133.327 | 136.047 | 3044406.347
140.65 | 171.226 | 174.72 | 3909807.318
147.695 | 179.803 | 183.472 | 4105653.025
146.279 | 178.078 | 181.712 | 4066272.385
134.8 | 164.104 | 167.453 | 3747185.331
116.145 | 141.394 | 144.28 | 3228619.967
87.154 | 106.101 | 108.266 | 2422726.876
47.237 | 57.505 | 58.679 | 1313088.292
10.679 | 13.001 | 13.266 | 296862.951
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
3.585 | 4.364 | 4.453 | 99650.386
48.656 | 59.234 | 60.443 | 1352557.701
105.825 | 128.83 | 131.459 | 2941731.812
79.06 | 96.246 | 98.211 | 2197709.881
123.456 | 150.294 | 153.361 | 3431843.775
148.519 | 180.806 | 184.496 | 4128558.881
144.356 | 175.737 | 179.324 | 4012820.648
125.889 | 153.256 | 156.383 | 3499476.152
91.817 | 111.777 | 114.058 | 2552338.925
48.683 | 59.266 | 60.475 | 1353291.058
13.503 | 16.438 | 16.774 | 375353.651
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.497 | 13.996 | 14.281 | 319586.886
39.954 | 48.639 | 49.632 | 1110638.358
98.339 | 119.717 | 122.16 | 2733641.181
145.078 | 176.617 | 180.221 | 4032903.909
158.492 | 192.946 | 196.884 | 4405773.76
153.133 | 186.422 | 190.227 | 4256804.072
143.287 | 174.436 | 177.996 | 3983108.901
121.559 | 147.985 | 151.005 | 3379117.66
91.447 | 111.327 | 113.599 | 2542061.578
49.433 | 60.179 | 61.408 | 1374144.951
12.117 | 14.751 | 15.052 | 336827.919
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.19 | 18.492 | 18.87 | 422253.796
78.643 | 95.74 | 97.693 | 2186137.944
121.85 | 148.339 | 151.367 | 3387206.023
144.623 | 176.063 | 179.656 | 4020255.657
155.066 | 188.776 | 192.629 | 4310550.625
155.377 | 189.154 | 193.015 | 4319187.072
143.487 | 174.68 | 178.245 | 3988677.22
121.534 | 147.955 | 150.974 | 3378428.172
90.656 | 110.363 | 112.616 | 2520058.992
49.064 | 59.73 | 60.949 | 1363887.347
12.311 | 14.987 | 15.293 | 342218.7
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.976 | 18.231 | 18.603 | 416294.157
77.165 | 93.94 | 95.858 | 2145048.409
114.656 | 139.582 | 142.43 | 3187235.506
134.756 | 164.05 | 167.398 | 3745955.494
143.907 | 175.191 | 178.766 | 4000345.551
142.034 | 172.911 | 176.44 | 3948284.798
131.134 | 159.642 | 162.9 | 3645293.326
107.885 | 131.338 | 134.018 | 2998998.073
80.039 | 97.439 | 99.427 | 2224937.718
44.867 | 54.621 | 55.736 | 1247226.101
11.141 | 13.563 | 13.84 | 309700.859
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
17.68 | 21.524 | 21.963 | 491478.821
60.316 | 73.429 | 74.927 | 1676684.733
121.744 | 148.21 | 151.235 | 3384258.525
150.582 | 183.317 | 187.058 | 4185897.52
155.551 | 189.366 | 193.231 | 4324025.386
159.508 | 194.184 | 198.147 | 4434034.153
148.734 | 181.068 | 184.763 | 4134538.263
129.312 | 157.424 | 160.636 | 3594643.3
93.044 | 113.271 | 115.583 | 2586453.797
48.303 | 58.804 | 60.004 | 1342739.669
13.949 | 16.982 | 17.328 | 387763.995
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
5.714 | 6.957 | 7.099 | 158852.363
33.18 | 40.393 | 41.218 | 922344.938
56.044 | 68.228 | 69.62 | 1557926.624
98.502 | 119.915 | 122.363 | 2738169.319
81.376 | 99.067 | 101.089 | 2262112.983
103.548 | 126.058 | 128.631 | 2878437.917
108.357 | 131.913 | 134.605 | 3012126.414
103.263 | 125.711 | 128.277 | 2870515.084
69.465 | 84.566 | 86.292 | 1930998.139
56.995 | 69.385 | 70.801 | 1584352.188
15.068 | 18.344 | 18.719 | 418871.109
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
17.056 | 20.764 | 21.188 | 474129.276
67.715 | 82.436 | 84.118 | 1882356.207
114.693 | 139.626 | 142.475 | 3188247.288
141.233 | 171.936 | 175.445 | 3926020.178
157.554 | 191.804 | 195.719 | 4379698.999
169.889 | 206.822 | 211.043 | 4722611.46
146.038 | 177.786 | 181.414 | 4059595.78
89.775 | 109.291 | 111.522 | 2495576.879
55.563 | 67.643 | 69.023 | 1544564.758
46.619 | 56.753 | 57.911 | 1295911.902
17.804 | 21.675 | 22.117 | 494926.151
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
2.889 | 3.517 | 3.589 | 80309.138
12.761 | 15.535 | 15.852 | 354729.931
37.148 | 45.223 | 46.146 | 1032635.482
95.026 | 115.684 | 118.045 | 2641550.817
95.746 | 116.56 | 118.939 | 2661557.427
93.235 | 113.503 | 115.819 | 2591751.426
106.376 | 129.501 | 132.144 | 2957053.52
75.794 | 92.271 | 94.154 | 2106933.74
73.328 | 89.268 | 91.09 | 2038369.694
61.537 | 74.915 | 76.443 | 1710617.684
18.273 | 22.245 | 22.699 | 507949.332
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.172 | 9.948 | 10.152 | 227162.22
53.434 | 65.05 | 66.378 | 1485367.164
76.854 | 93.562 | 95.471 | 2136407.579
144.248 | 175.606 | 179.19 | 4009824.898
124.203 | 151.204 | 154.29 | 3452620.907
45.042 | 54.833 | 55.952 | 1252072.15
118.319 | 144.04 | 146.98 | 3289043.125
110.439 | 134.448 | 137.191 | 3070005.402
90.192 | 109.799 | 112.04 | 2507172.832
38.07 | 46.346 | 47.292 | 1058275.054
22.724 | 27.664 | 28.228 | 631682.776
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
21.684 | 26.397 | 26.936 | 602761.404
74.424 | 90.604 | 92.453 | 2068863.971
118.982 | 144.848 | 147.804 | 3307485.486
145.616 | 177.271 | 180.889 | 4047846.415
152.69 | 185.884 | 189.677 | 4244506.513
150.952 | 183.768 | 187.518 | 4196191.258
139.645 | 170.002 | 173.472 | 3881865.867
118.347 | 144.074 | 147.015 | 3289821.382
88.351 | 107.558 | 109.753 | 2455998.848
49.443 | 60.192 | 61.42 | 1374431.001
12.724 | 15.49 | 15.806 | 353701.758
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
22.411 | 27.284 | 27.84 | 622998.077
80.98 | 98.585 | 100.597 | 2251105.631
120.344 | 146.506 | 149.496 | 3345345.856
140.383 | 170.902 | 174.389 | 3902400.708
149.173 | 181.602 | 185.309 | 4146739.318
147.466 | 179.524 | 183.188 | 4099286.706
136.049 | 165.625 | 169.005 | 3781912.93
115.999 | 141.216 | 144.098 | 3224555.527
86.634 | 105.467 | 107.619 | 2408255.803
48.047 | 58.492 | 59.685 | 1335614.836
11.93 | 14.523 | 14.82 | 331626.794
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
2.402 | 2.925 | 2.984 | 66781.742
68.227 | 83.059 | 84.754 | 1896585.099
118.865 | 144.706 | 147.659 | 3304239.82
151.62 | 184.581 | 188.348 | 4214758.632
93.34 | 113.632 | 115.951 | 2594691.189
79.584 | 96.885 | 98.862 | 2212289.466
42.885 | 52.208 | 53.273 | 1192124.698
24.694 | 30.062 | 30.676 | 686445.494
66.743 | 81.252 | 82.911 | 1855330.034
63.086 | 76.8 | 78.368 | 1753671.554
24.634 | 29.99 | 30.602 | 684792.476
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
5.722 | 6.966 | 7.108 | 159061.762
53.504 | 65.136 | 66.465 | 1487322.623
113.983 | 138.762 | 141.594 | 3168519.103
122.044 | 148.575 | 151.607 | 3392592.421
169.885 | 206.816 | 211.037 | 4722482.174
141.131 | 171.812 | 175.318 | 3923185.575
112.489 | 136.943 | 139.737 | 3126981.23
74.334 | 90.494 | 92.341 | 2066356.045
54.617 | 66.49 | 67.847 | 1518247.816
47.22 | 57.485 | 58.658 | 1312624.594
13.983 | 17.023 | 17.37 | 388703.399
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
25.516 | 31.063 | 31.697 | 709298.715
80.732 | 98.282 | 100.288 | 2244194.58
125.315 | 152.557 | 155.67 | 3483517.591
147.411 | 179.457 | 183.119 | 4097754.318
153.995 | 187.472 | 191.298 | 4280774.235
150.249 | 182.911 | 186.644 | 4176631.955
139.264 | 169.539 | 172.999 | 3871285.969
119.056 | 144.938 | 147.896 | 3309541.832
90.224 | 109.838 | 112.08 | 2508063.984
50.942 | 62.017 | 63.282 | 1416101.512
13.418 | 16.335 | 16.668 | 372994.754
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
26.295 | 32.011 | 32.664 | 730946.225
82.751 | 100.74 | 102.796 | 2300319.773
126.131 | 153.551 | 156.685 | 3506214.048
148.385 | 180.642 | 184.329 | 4124821.118
157.32 | 191.52 | 195.429 | 4373207.667
155.136 | 188.862 | 192.716 | 4312506.084
144.183 | 175.528 | 179.11 | 4008034.859
123.072 | 149.827 | 152.885 | 3421179.491
92.063 | 112.077 | 114.364 | 2559185.333
51.128 | 62.243 | 63.513 | 1421266.503
13.028 | 15.86 | 16.184 | 362152.932
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
25.385 | 30.904 | 31.534 | 705661.729
82.164 | 100.026 | 102.067 | 2284010.409
126.809 | 154.376 | 157.527 | 3525055.464
148.909 | 181.281 | 184.98 | 4139400.703
165.711 | 201.735 | 205.852 | 4606457.781
166.253 | 202.395 | 206.525 | 4621525.19
145.764 | 177.452 | 181.074 | 4051975.498
123.925 | 150.865 | 153.944 | 3444883.347
93.839 | 114.238 | 116.57 | 2608540.879
54.71 | 66.604 | 67.963 | 1520844.511
17.183 | 20.918 | 21.345 | 477648.984
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
26.178 | 31.869 | 32.519 | 727700.559
84.395 | 102.742 | 104.838 | 2346026.215
128.757 | 156.748 | 159.947 | 3579213.08
152.112 | 185.179 | 188.959 | 4228423.049
161.843 | 197.027 | 201.048 | 4498949.205
169.661 | 206.543 | 210.759 | 4716252.876
144.655 | 176.101 | 179.695 | 4021130.418
134.342 | 163.547 | 166.884 | 3734460.318
96.957 | 118.035 | 120.443 | 2695228.344
53.005 | 64.527 | 65.844 | 1473428.143
14.005 | 17.05 | 17.398 | 389320.509
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
23.146 | 28.178 | 28.753 | 643420.133
80.281 | 97.733 | 99.728 | 2231659.223
126.55 | 154.061 | 157.205 | 3517858.253
145.559 | 177.202 | 180.818 | 4046265.775
150.552 | 183.281 | 187.021 | 4185071.011
147.277 | 179.294 | 182.953 | 4094032.946
138.639 | 168.778 | 172.222 | 3853907.915
123.715 | 150.61 | 153.683 | 3439052.994
93.111 | 113.352 | 115.666 | 2588308.479
49.98 | 60.846 | 62.088 | 1389365.772
12.867 | 15.664 | 15.984 | 357677.429
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
22.003 | 26.786 | 27.332 | 611635.649
69.758 | 84.922 | 86.656 | 1939134.754
116.143 | 141.391 | 144.277 | 3228555.324
149.594 | 182.114 | 185.831 | 4158431.775
163.95 | 199.592 | 203.665 | 4557517.681
161.606 | 196.737 | 200.752 | 4492336.322
149.23 | 181.671 | 185.379 | 4148315.575
127.445 | 155.151 | 158.317 | 3542743.694
95.693 | 116.496 | 118.874 | 2660094.065
52.697 | 64.153 | 65.463 | 1464884.848
13.365 | 16.271 | 16.603 | 371531.392
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
16.344 | 19.898 | 20.304 | 454348.456
76.573 | 93.22 | 95.122 | 2128597.641
98.674 | 120.125 | 122.576 | 2742954.998
108.24 | 131.77 | 134.46 | 3008868.74
154.577 | 188.181 | 192.021 | 4296958.586
164.48 | 200.236 | 204.323 | 4572234.397
153.246 | 186.561 | 190.368 | 4259965.242
133.065 | 161.992 | 165.298 | 3698958.845
98.982 | 120.499 | 122.959 | 2751507.059
52.556 | 63.981 | 65.287 | 1460957.429
14.233 | 17.328 | 17.681 | 395662.702
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
22.787 | 27.74 | 28.306 | 633424.563
80.292 | 97.747 | 99.742 | 2231973.782
127.071 | 154.695 | 157.852 | 3532337.061
158.072 | 192.436 | 196.363 | 4394117.437
167.9 | 204.4 | 208.572 | 4667312.776
165.999 | 202.086 | 206.21 | 4614469.383
149.699 | 182.243 | 185.962 | 4161367.155
128.057 | 155.895 | 159.077 | 3559742.546
80.116 | 97.532 | 99.523 | 2227070.825
50.656 | 61.668 | 62.926 | 1408138.162
20.734 | 25.241 | 25.756 | 576359.966
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
18.41 | 22.413 | 22.87 | 511775.864
49.942 | 60.799 | 62.04 | 1388297.082
93.702 | 114.072 | 116.4 | 2604742.746
148.305 | 180.545 | 184.23 | 4122603.625
163.756 | 199.355 | 203.424 | 4552114.892
173.292 | 210.965 | 215.27 | 4817209.75
165.25 | 201.174 | 205.279 | 4593643.999
132.22 | 160.963 | 164.248 | 3675464.388
99.281 | 120.864 | 123.331 | 2759833.22
53.065 | 64.601 | 65.92 | 1475113.943
16.299 | 19.843 | 20.248 | 453094.493
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
20.117 | 24.49 | 24.99 | 559212.085
71.791 | 87.398 | 89.182 | 1995663.275
117.864 | 143.486 | 146.415 | 3276394.873
147.829 | 179.966 | 183.639 | 4109378.78
161.954 | 197.162 | 201.185 | 4502029.341
159.119 | 193.71 | 197.663 | 4423212.074
150.404 | 183.101 | 186.837 | 4180958.319
131.617 | 160.229 | 163.499 | 3658703.444
64.188 | 78.142 | 79.737 | 1784310.587
39.305 | 47.849 | 48.825 | 1092594.942
13.944 | 16.976 | 17.322 | 387626.974
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
3.897 | 4.744 | 4.841 | 108327.35
61.956 | 75.425 | 76.964 | 1722266.272
111.629 | 135.896 | 138.67 | 3103080.093
161.244 | 196.298 | 200.304 | 4482301.156
180.78 | 220.079 | 224.571 | 5025336.625
174.933 | 212.962 | 217.308 | 4862815.415
147.368 | 179.404 | 183.066 | 4096552.99
98.777 | 120.25 | 122.704 | 2745813.727
42.736 | 52.026 | 53.088 | 1187975.872
7.974 | 9.708 | 9.906 | 221670.552
0.358 | 0.435 | 0.444 | 9938.662
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.822 | 2.218 | 2.263 | 50645.643
14.136 | 17.209 | 17.56 | 392953.112
40.88 | 49.767 | 50.782 | 1136386.442
34.914 | 42.504 | 43.372 | 970547.298
39.474 | 48.056 | 49.036 | 1097312.626
26.717 | 32.525 | 33.189 | 742683.582
66.469 | 80.919 | 82.571 | 1847721.76
46.501 | 56.61 | 57.766 | 1292646.493
65.554 | 79.804 | 81.433 | 1822267.461
25.951 | 31.593 | 32.238 | 721398.883
15.216 | 18.523 | 18.901 | 422963.027
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
31.814 | 38.73 | 39.52 | 884367.29
88.447 | 107.674 | 109.872 | 2458655.913
128.132 | 155.987 | 159.171 | 3561839.409
153.73 | 187.149 | 190.969 | 4273403.869
162.037 | 197.262 | 201.288 | 4504323.595
173.97 | 211.789 | 216.112 | 4836039.158
118.14 | 143.822 | 146.757 | 3284063.407
84.835 | 103.277 | 105.384 | 2358247.013
65.073 | 79.22 | 80.836 | 1808917.603
54.588 | 66.455 | 67.811 | 1517445.433
17.068 | 20.779 | 21.203 | 474467.961
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
24.26 | 29.534 | 30.136 | 674381.46
88.854 | 108.17 | 110.377 | 2469973.441
130.326 | 158.658 | 161.896 | 3622827.042
139.38 | 169.68 | 173.143 | 3874507.509
148.189 | 180.404 | 184.086 | 4119382.085
157.095 | 191.246 | 195.149 | 4366949.86
151.832 | 184.839 | 188.611 | 4220649.245
128.045 | 155.881 | 159.062 | 3559415.869
98.294 | 119.663 | 122.105 | 2732403.609
53.11 | 64.656 | 65.976 | 1476367.906
14.081 | 17.142 | 17.492 | 391425.107
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
27.701 | 33.722 | 34.411 | 770024.424
80.919 | 98.511 | 100.521 | 2249412.096
124.21 | 151.212 | 154.298 | 3452806.18
155.896 | 189.786 | 193.659 | 4333613.245
169.311 | 206.118 | 210.325 | 4706540.004
165.582 | 201.579 | 205.692 | 4602885.438
153.098 | 186.38 | 190.184 | 4255840.542
133.202 | 162.159 | 165.468 | 3702768.986
100.522 | 122.375 | 124.872 | 2794330.646
53.669 | 65.337 | 66.67 | 1491911.021
15.205 | 18.51 | 18.888 | 422664.859
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
28.742 | 34.99 | 35.704 | 798969.922
84.775 | 103.204 | 105.311 | 2356586.37
130.545 | 158.925 | 162.168 | 3628919.319
160.425 | 195.3 | 199.286 | 4459520.313
165.553 | 201.543 | 205.656 | 4602071.047
164.628 | 200.417 | 204.507 | 4576359.097
152.532 | 185.691 | 189.481 | 4240107.771
133.68 | 162.741 | 166.062 | 3716058.474
100.109 | 121.872 | 124.359 | 2782847.588
53.718 | 65.396 | 66.731 | 1493265.871
14.408 | 17.54 | 17.898 | 400513.134
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
34.511 | 42.014 | 42.871 | 959350.29
88.218 | 107.396 | 109.587 | 2452297.219
131.254 | 159.788 | 163.049 | 3648627.761
150.733 | 183.502 | 187.246 | 4190110.989
156.63 | 190.68 | 194.571 | 4354023.183
150.943 | 183.757 | 187.507 | 4195941.342
149.035 | 181.434 | 185.137 | 4142900.668
128.548 | 156.493 | 159.687 | 3573394.845
100.49 | 122.336 | 124.832 | 2793439.494
51.383 | 62.553 | 63.83 | 1428350.819
17.106 | 20.825 | 21.25 | 475520.26
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
37.26 | 45.36 | 46.286 | 1035760.518
94.014 | 114.451 | 116.787 | 2613403.319
122.27 | 148.851 | 151.888 | 3398886.362
149.208 | 181.644 | 185.351 | 4147698.465
153.265 | 186.583 | 190.391 | 4260477.192
154.687 | 188.315 | 192.158 | 4300018.979
143.758 | 175.01 | 178.581 | 3996208.733
121.185 | 147.529 | 150.54 | 3368711.027
95.01 | 115.664 | 118.025 | 2641099.237
54.617 | 66.491 | 67.848 | 1518264.207
16.094 | 19.592 | 19.992 | 447372.762
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.825 | 11.961 | 12.205 | 273118.578
47.437 | 57.749 | 58.928 | 1318656.611
45.111 | 54.918 | 56.039 | 1254007.866
66.54 | 81.005 | 82.659 | 1849689.337
123.893 | 150.826 | 153.904 | 3443992.195
157.025 | 191.16 | 195.061 | 4364990.018
141.479 | 172.235 | 175.75 | 3932850.195
118.361 | 144.092 | 147.032 | 3290220.327
65.796 | 80.099 | 81.734 | 1829000.974
38.303 | 46.63 | 47.582 | 1064758.651
13.614 | 16.574 | 16.912 | 378450.178
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
21.639 | 26.344 | 26.881 | 601535.84
71.856 | 87.477 | 89.262 | 1997465.322
115.706 | 140.86 | 143.735 | 3216423.295
142.833 | 173.884 | 177.433 | 3970501.166
159.025 | 193.596 | 197.547 | 4420607.644
156.595 | 190.638 | 194.529 | 4353064.036
149.279 | 181.731 | 185.44 | 4149682.433
129.866 | 158.097 | 161.324 | 3610025.378
96.105 | 116.998 | 119.386 | 2671552.997
52.963 | 64.477 | 65.793 | 1472279.34
16.367 | 19.925 | 20.331 | 454968.918
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.848 | 13.206 | 13.476 | 301552.236
37.951 | 46.201 | 47.144 | 1054964.745
110.3 | 134.278 | 137.018 | 3066130.618
167.215 | 203.566 | 207.721 | 4648269.696
151.513 | 184.451 | 188.215 | 4211787.008
162.307 | 197.591 | 201.624 | 4511835.365
145.329 | 176.923 | 180.533 | 4039887.338
123.162 | 149.936 | 152.996 | 3423671.026
92.244 | 112.297 | 114.589 | 2564213.303
52.261 | 63.622 | 64.921 | 1452760.554
12.649 | 15.399 | 15.714 | 351625.669
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
38.329 | 46.662 | 47.614 | 1065484.273
93.822 | 114.217 | 116.548 | 2608060.79
135.248 | 164.65 | 168.01 | 3759648.31
154.288 | 187.829 | 191.663 | 4288927.241
160.883 | 195.858 | 199.855 | 4472257.334
158.266 | 192.672 | 196.604 | 4399508.218
147.224 | 179.229 | 182.886 | 4092548.81
127.925 | 155.734 | 158.913 | 3556069.426
96.584 | 117.58 | 119.98 | 2684850.22
53.504 | 65.135 | 66.464 | 1487306.232
13.294 | 16.184 | 16.515 | 369551.807
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
25.31 | 30.812 | 31.441 | 703569.249
62.95 | 76.635 | 78.199 | 1749897.547
91.975 | 111.969 | 114.254 | 2556725.659
132.383 | 161.162 | 164.451 | 3680004.534
173.958 | 211.775 | 216.097 | 4835712.481
149.054 | 181.458 | 185.161 | 4143441.017
129.182 | 157.264 | 160.474 | 3591006.424
127.306 | 154.981 | 158.144 | 3538868.91
74.763 | 91.016 | 92.873 | 2078274.292
51.37 | 62.537 | 63.814 | 1427988.008
16.969 | 20.658 | 21.079 | 471705.736
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
34.822 | 42.392 | 43.257 | 967986.737
90.136 | 109.731 | 111.97 | 2505616.318
132.069 | 160.78 | 164.061 | 3671279.318
156.741 | 190.816 | 194.71 | 4357124.093
166.078 | 202.182 | 206.308 | 4616662.75
161.69 | 196.84 | 200.858 | 4494687.484
152.009 | 185.054 | 188.831 | 4225564.32
129.494 | 157.645 | 160.862 | 3599695.396
98.756 | 120.224 | 122.678 | 2745225.126
51.345 | 62.507 | 63.783 | 1427298.52
14.096 | 17.16 | 17.51 | 391836.17
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
30.539 | 37.179 | 37.937 | 848942.468
82.312 | 100.205 | 102.25 | 2288106.71
128.692 | 156.669 | 159.866 | 3577406.65
157.192 | 191.364 | 195.269 | 4369643.059
171.27 | 208.503 | 212.758 | 4760995.788
172.875 | 210.456 | 214.751 | 4805597.406
159.696 | 194.412 | 198.38 | 4439247.396
136.612 | 166.31 | 169.704 | 3797556.932
99.631 | 121.29 | 123.765 | 2769558.1
52.63 | 64.071 | 65.378 | 1463009.392
25.656 | 31.234 | 31.871 | 713197.625
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
31.169 | 37.945 | 38.719 | 866441.152
81.741 | 99.511 | 101.542 | 2272253.309
125.037 | 152.219 | 155.326 | 3475800.805
153.574 | 186.959 | 190.775 | 4269065.387
168.104 | 204.648 | 208.825 | 4672977.599
166.833 | 203.101 | 207.245 | 4637644.898
155.656 | 189.494 | 193.361 | 4326944.375
135.034 | 164.389 | 167.744 | 3753693.054
97.282 | 118.431 | 120.848 | 2704272.502
52.132 | 63.465 | 64.76 | 1449171.82
14.745 | 17.951 | 18.317 | 409891.594
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
35.484 | 43.198 | 44.08 | 986392.964
88.176 | 107.345 | 109.535 | 2451132.025
130.832 | 159.273 | 162.524 | 3636878.396
155.914 | 189.808 | 193.682 | 4334117.46
160.366 | 195.228 | 199.213 | 4457879.413
157.026 | 191.162 | 195.064 | 4365034.918
139.752 | 170.132 | 173.604 | 3884833.108
118.597 | 144.379 | 147.326 | 3296780.685
91.214 | 111.043 | 113.31 | 2535582.364
49.92 | 60.772 | 62.012 | 1387679.972
12.658 | 15.409 | 15.724 | 351859.194
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
35.565 | 43.296 | 44.18 | 988634.583
94.607 | 115.174 | 117.524 | 2629902.229
133.726 | 162.797 | 166.12 | 3717340.946
150.335 | 183.017 | 186.752 | 4179043.377
156.267 | 190.238 | 194.12 | 4343931.109
134.388 | 163.602 | 166.941 | 3735726.399
95.007 | 115.661 | 118.021 | 2641022.476
131.388 | 159.951 | 163.215 | 3652349.133
95.149 | 115.833 | 118.197 | 2644957.63
42.471 | 51.704 | 52.759 | 1180617.514
18.444 | 22.454 | 22.912 | 512715.268
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
21.71 | 26.43 | 26.969 | 603503.417
62.222 | 75.748 | 77.294 | 1729648.756
107.284 | 130.606 | 133.272 | 2982289.764
131.573 | 160.175 | 163.444 | 3657473.607
130.329 | 158.662 | 161.9 | 3622915.811
132.877 | 161.763 | 165.064 | 3693729.211
150.715 | 183.479 | 187.223 | 4189594.766
127.647 | 155.396 | 158.567 | 3548343.874
94.812 | 115.424 | 117.779 | 2635607.569
51.003 | 62.09 | 63.358 | 1417783.039
15.133 | 18.423 | 18.799 | 420673.156
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
29.261 | 35.622 | 36.349 | 813400.478
76.99 | 93.727 | 95.64 | 2140181.586
117.162 | 142.632 | 145.543 | 3256888.095
143.038 | 174.133 | 177.687 | 3976190.115
157.265 | 191.452 | 195.36 | 4371663.271
157.564 | 191.817 | 195.732 | 4379989.432
147.946 | 180.109 | 183.784 | 4112636.454
127.273 | 154.941 | 158.103 | 3537953.632
93.355 | 113.65 | 115.969 | 2595102.252
48.347 | 58.857 | 60.058 | 1343953.115
16.918 | 20.596 | 21.016 | 470290.626
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.079 | 11.052 | 11.278 | 252369.955
51.182 | 62.309 | 63.58 | 1422770.382
68.912 | 83.893 | 85.605 | 1915628.179
117.01 | 142.447 | 145.354 | 3252662.508
149.318 | 181.779 | 185.488 | 4150770.866
123.674 | 150.56 | 153.632 | 3437911.926
150.389 | 183.083 | 186.819 | 4180547.256
134.347 | 163.553 | 166.89 | 3734597.339
92.784 | 112.955 | 115.26 | 2579232.46
54.161 | 65.935 | 67.281 | 1505575.438
20.879 | 25.418 | 25.936 | 580395.897
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
45.084 | 54.885 | 56.005 | 1253253.735
96.303 | 117.239 | 119.632 | 2677056.673
125.851 | 153.21 | 156.336 | 3498423.853
144.37 | 175.754 | 179.341 | 4013207.585
168.678 | 205.347 | 209.538 | 4688936.16
163.624 | 199.194 | 203.259 | 4548437.389
152.022 | 185.07 | 188.847 | 4225927.131
127.554 | 155.283 | 158.452 | 3545763.57
95.322 | 116.045 | 118.413 | 2649788.209
57.319 | 69.78 | 71.204 | 1593367.837
19.631 | 23.899 | 24.387 | 545713.198
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
29.974 | 36.49 | 37.235 | 833221.815
43.386 | 52.818 | 53.896 | 1206055.422
62.27 | 75.807 | 77.354 | 1730991.488
68.424 | 83.299 | 84.999 | 1902064.649
45.603 | 55.517 | 56.65 | 1267684.291
49.022 | 59.678 | 60.896 | 1362705.762
43.812 | 53.336 | 54.425 | 1217889.283
54.416 | 66.245 | 67.597 | 1512655.371
46.21 | 56.256 | 57.404 | 1284558.13
32.364 | 39.4 | 40.204 | 899664.872
12.668 | 15.421 | 15.736 | 352133.236
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.18 | 0.219 | 0.223 | 4999.461
50.796 | 61.838 | 63.1 | 1412025.064
100.264 | 122.06 | 124.551 | 2787145.553
134.955 | 164.293 | 167.646 | 3751499.687
159.66 | 194.369 | 198.336 | 4438259.74
164.701 | 200.506 | 204.598 | 4578391.317
163.794 | 199.402 | 203.471 | 4553179.199
166.677 | 202.911 | 207.052 | 4633310.799
117.393 | 142.913 | 145.83 | 3263307.049
69.076 | 84.093 | 85.809 | 1920192.451
33.681 | 41.003 | 41.84 | 936271.279
9.494 | 11.558 | 11.794 | 263917.656
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.777 | 0.946 | 0.965 | 21599.258
43.471 | 52.921 | 54.001 | 1208409.936
98.503 | 119.917 | 122.364 | 2738205.453
144.767 | 176.238 | 179.835 | 4024255.454
143.126 | 174.241 | 177.797 | 3978649.789
171.1 | 208.295 | 212.546 | 4756253.978
168.128 | 204.677 | 208.855 | 4673642.961
157.892 | 192.216 | 196.139 | 4389101.585
136.937 | 166.706 | 170.109 | 3806601.09
102.817 | 125.169 | 127.723 | 2858128.756
56.441 | 68.711 | 70.114 | 1568962.485
17.209 | 20.95 | 21.378 | 478378.989
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.363 | 0.441 | 0.45 | 10075.683
43.952 | 53.507 | 54.599 | 1221788.193
94.436 | 114.965 | 117.311 | 2625136.293
137.663 | 167.589 | 171.009 | 3826764.464
167.502 | 203.915 | 208.077 | 4656240.781
181.533 | 220.997 | 225.507 | 5046286.912
181.229 | 220.626 | 225.129 | 5037823.73
167.928 | 204.434 | 208.606 | 4668086.65
143.968 | 175.266 | 178.843 | 4002055.477
107.858 | 131.305 | 133.985 | 2998248.325
64.526 | 78.553 | 80.157 | 1793701.165
19.96 | 24.299 | 24.795 | 554849.477
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.525 | 1.856 | 1.894 | 42384.125
43.928 | 53.478 | 54.569 | 1221122.831
94.882 | 115.509 | 117.866 | 2637551.02
135.618 | 165.1 | 168.469 | 3769925.657
161.3 | 196.365 | 200.372 | 4483836.896
174.276 | 212.162 | 216.492 | 4844550.592
172.046 | 209.447 | 213.722 | 4782558.912
159.155 | 193.754 | 197.708 | 4424216.121
136.946 | 166.717 | 170.119 | 3806846.623
104.226 | 126.883 | 129.473 | 2897279.333
63.154 | 76.883 | 78.452 | 1755562.37
16.204 | 19.726 | 20.129 | 450433.155
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
51.231 | 62.368 | 63.641 | 1424125.232
97.568 | 118.779 | 121.203 | 2712219.461
131.448 | 160.024 | 163.29 | 3654018.542
150.802 | 183.585 | 187.332 | 4192018.306
159.759 | 194.49 | 198.459 | 4441017.582
158.566 | 193.036 | 196.976 | 4407830.106
149.779 | 182.34 | 186.061 | 4163584.648
132.786 | 161.652 | 164.951 | 3691197.159
80.913 | 98.503 | 100.513 | 2249234.558
51.576 | 62.788 | 64.07 | 1433717.474
22.343 | 27.2 | 27.755 | 621090.87
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.168 | 1.421 | 1.45 | 32453.198
46.76 | 56.925 | 58.087 | 1299839.321
94.03 | 114.471 | 116.807 | 2613854.899
130.815 | 159.252 | 162.503 | 3636402.69
146.522 | 178.374 | 182.015 | 4073034.407
150.781 | 183.56 | 187.306 | 4191441.713
148.18 | 180.393 | 184.075 | 4119132.169
136.856 | 166.607 | 170.008 | 3804343.08
119.275 | 145.204 | 148.167 | 3315617.718
89.695 | 109.194 | 111.422 | 2493355.003
49.121 | 59.8 | 61.02 | 1365479.995
10.906 | 13.277 | 13.548 | 303169.01
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.86 | 1.047 | 1.068 | 23905.52
29.881 | 36.377 | 37.119 | 830637.128
67.296 | 81.926 | 83.598 | 1870712.002
121.877 | 148.372 | 151.4 | 3387955.771
150.572 | 183.305 | 187.046 | 4185623.478
161.626 | 196.762 | 200.777 | 4492900.797
157.056 | 191.198 | 195.1 | 4365857.044
145.402 | 177.011 | 180.623 | 4041903.167
124.494 | 151.558 | 154.651 | 3460704.887
92.395 | 112.48 | 114.776 | 2568398.373
47.85 | 58.253 | 59.441 | 1330151.677
10.923 | 13.297 | 13.568 | 303628.325
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
7.398 | 9.006 | 9.189 | 205642.965
39.356 | 47.911 | 48.889 | 1094014.435
86.208 | 104.949 | 107.09 | 2396421.942
120.748 | 146.998 | 149.998 | 3356578.998
141.488 | 172.247 | 175.762 | 3933116.502
154.478 | 188.06 | 191.898 | 4294200.744
150.421 | 183.122 | 186.859 | 4181438.408
138.045 | 168.055 | 171.485 | 3837401.27
109.318 | 133.082 | 135.798 | 3038826.02
89.205 | 108.597 | 110.813 | 2479726.83
48.367 | 58.882 | 60.083 | 1344517.59
10.178 | 12.391 | 12.644 | 282936.61
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
2.853 | 3.474 | 3.545 | 79321.482
40.232 | 48.979 | 49.978 | 1118387.926
80.761 | 98.317 | 100.324 | 2244996.963
104.935 | 127.747 | 130.354 | 2916999.783
152.038 | 185.09 | 188.867 | 4226378.711
168.808 | 205.505 | 209.699 | 4692544.637
167.07 | 203.389 | 207.54 | 4644229.382
157.3 | 191.496 | 195.404 | 4372655.2
133.236 | 162.201 | 165.511 | 3703724.781
100.29 | 122.092 | 124.583 | 2787871.175
56.809 | 69.158 | 70.57 | 1579175.189
18.13 | 22.071 | 22.522 | 503978.044
4.385 | 5.338 | 5.447 | 121890.88
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
5.954 | 7.249 | 7.397 | 165521.233
48.759 | 59.359 | 60.57 | 1355412.047
95.049 | 115.712 | 118.074 | 2642192.053
96.325 | 117.265 | 119.658 | 2677653.009
156.445 | 190.455 | 194.342 | 4348886.701
179.48 | 218.498 | 222.957 | 4989222.315
177.098 | 215.597 | 219.997 | 4922988.657
163.643 | 199.217 | 203.283 | 4548965.73
137.939 | 167.926 | 171.353 | 3834453.772
99.026 | 120.554 | 123.014 | 2752748.904
52.193 | 63.539 | 64.836 | 1450865.355
20.814 | 25.339 | 25.857 | 578598.233
4.954 | 6.03 | 6.154 | 137700.412
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.646 | 11.743 | 11.983 | 268143.243
50.243 | 61.166 | 62.414 | 1396671.495
96.69 | 117.71 | 120.112 | 2687809.726
133.824 | 162.917 | 166.242 | 3720074.662
158.695 | 193.194 | 197.136 | 4411426.465
162.22 | 197.486 | 201.516 | 4509428.216
171.925 | 209.3 | 213.572 | 4779200.351
158.47 | 192.92 | 196.857 | 4405173.041
136.291 | 165.92 | 169.306 | 3788646.443
100.218 | 122.005 | 124.495 | 2785883.855
58.364 | 71.052 | 72.502 | 1622414.222
20.244 | 24.645 | 25.148 | 562748.184
4.757 | 5.791 | 5.909 | 132232.87
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
3.32 | 4.042 | 4.124 | 92292.028
37.177 | 45.259 | 46.182 | 1033449.873
86.574 | 105.395 | 107.546 | 2406607.168
129.467 | 157.612 | 160.829 | 3598945.648
157.563 | 191.816 | 195.731 | 4379965.306
171.979 | 209.366 | 213.639 | 4780704.23
174.341 | 212.241 | 216.572 | 4846352.639
161.459 | 196.559 | 200.571 | 4488268.53
137.217 | 167.047 | 170.456 | 3814382.519
102.142 | 124.347 | 126.885 | 2839364.101
58.031 | 70.647 | 72.088 | 1613160.665
17.47 | 21.268 | 21.702 | 485636.46
3.025 | 3.683 | 3.758 | 84095.153
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.073 | 12.263 | 12.513 | 280013.238
52.541 | 63.963 | 65.268 | 1460541.983
101.718 | 123.831 | 126.358 | 2827578.492
140.351 | 170.862 | 174.349 | 3901497.548
164.468 | 200.222 | 204.308 | 4571907.72
172.412 | 209.893 | 214.176 | 4792735.372
167.847 | 204.336 | 208.506 | 4665845.031
151.886 | 184.904 | 188.678 | 4222141.116
127.792 | 155.572 | 158.747 | 3552367.797
92.567 | 112.691 | 114.99 | 2573200.443
52.551 | 63.975 | 65.281 | 1460820.408
15.712 | 19.127 | 19.518 | 436756.73
4.275 | 5.204 | 5.31 | 118830.487
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.107 | 9.869 | 10.071 | 225355.79
48.713 | 59.303 | 60.513 | 1354133.958
97.168 | 118.292 | 120.706 | 2701099.214
133.3 | 162.278 | 165.59 | 3705490.694
155.978 | 189.886 | 193.761 | 4335895.381
162.26 | 197.534 | 201.565 | 4510528.767
157.299 | 191.494 | 195.402 | 4372614.683
146.677 | 178.563 | 182.208 | 4077348.763
123.724 | 150.62 | 153.694 | 3439290.902
91.461 | 111.344 | 113.616 | 2542448.515
52.877 | 64.372 | 65.686 | 1469884.309
19.7 | 23.983 | 24.472 | 547628.14
5.503 | 6.699 | 6.836 | 152969.485
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
7.15 | 8.704 | 8.881 | 198748.305
42.867 | 52.186 | 53.251 | 1191624.866
76.96 | 93.69 | 95.602 | 2139338.686
102.8 | 125.148 | 127.702 | 2857653.05
113.089 | 137.673 | 140.483 | 3143657.788
127.237 | 154.897 | 158.058 | 3536949.585
155.379 | 189.157 | 193.018 | 4319251.715
148.036 | 180.218 | 183.896 | 4115132.372
122.615 | 149.271 | 152.317 | 3408478.604
92.403 | 112.49 | 114.786 | 2568624.163
37.24 | 45.335 | 46.261 | 1035196.043
19.495 | 23.733 | 24.218 | 541927.183
2.833 | 3.449 | 3.519 | 78752.624
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
3.161 | 3.848 | 3.927 | 87869.16
17.246 | 20.995 | 21.424 | 479407.162
26.476 | 32.232 | 32.89 | 735990.586
31.127 | 37.894 | 38.667 | 865275.958
33.783 | 41.127 | 41.966 | 939101.499
34.839 | 42.413 | 43.279 | 968466.826
34.006 | 41.398 | 42.243 | 945294.663
32.806 | 39.937 | 40.752 | 911933.922
30.593 | 37.243 | 38.003 | 850417.948
27.759 | 33.794 | 34.483 | 771653.206
22.822 | 27.783 | 28.35 | 634404.484
14.276 | 17.38 | 17.735 | 396856.405
4.616 | 5.62 | 5.734 | 128321.842
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
6.271 | 7.634 | 7.79 | 174318.827
41.84 | 50.935 | 51.975 | 1163066.305
92.26 | 112.316 | 114.608 | 2564648.492
138.432 | 168.525 | 171.965 | 3848142.315
165.453 | 201.421 | 205.531 | 4599284.696
177.332 | 215.882 | 220.288 | 4929496.38
174.403 | 212.317 | 216.65 | 4848086.691
159.343 | 193.983 | 197.941 | 4429441.372
139.268 | 169.543 | 173.003 | 3871382.473
105.669 | 128.641 | 131.266 | 2937409.721
64.477 | 78.494 | 80.096 | 1792346.315
23.741 | 28.902 | 29.492 | 659955.287
8.056 | 9.807 | 10.007 | 223936.297
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.538 | 10.394 | 10.606 | 237338.68
53.56 | 65.203 | 66.534 | 1488862.746
102.422 | 124.688 | 127.233 | 2847149.913
142.375 | 173.326 | 176.864 | 3957764.145
165.676 | 201.693 | 205.809 | 4605494.251
176.887 | 215.341 | 219.735 | 4917134.178
176.804 | 215.239 | 219.632 | 4914815.908
164.046 | 199.708 | 203.784 | 4560174.746
138.818 | 168.995 | 172.444 | 3858871.242
103.391 | 125.867 | 128.436 | 2874075.309
60.263 | 73.363 | 74.861 | 1675192.972
21.17 | 25.772 | 26.298 | 588484.26
6.689 | 8.143 | 8.309 | 185938.906
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.375 | 16.283 | 16.615 | 371805.434
54.468 | 66.309 | 67.662 | 1514110.998
101.119 | 123.102 | 125.614 | 2810930.443
138.084 | 168.103 | 171.533 | 3838489.703
163.249 | 198.738 | 202.794 | 4538023.021
175.763 | 213.972 | 218.339 | 4885882.418
177.539 | 216.134 | 220.545 | 4935249.972
163.563 | 199.12 | 203.183 | 4546743.854
139.721 | 170.095 | 173.566 | 3883982.473
103.898 | 126.484 | 129.066 | 2888167.18
61.77 | 75.199 | 76.733 | 1717101.281
18.416 | 22.419 | 22.877 | 511925.003
8.214 | 9.999 | 10.203 | 228323.031
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.355 | 17.475 | 17.832 | 399033.381
57.924 | 70.516 | 71.955 | 1610177.033
99.371 | 120.974 | 123.443 | 2762341.146
139.634 | 169.989 | 173.458 | 3881563.316
164.066 | 199.732 | 203.808 | 4560722.83
177.647 | 216.266 | 220.679 | 4938257.73
177.416 | 215.984 | 220.392 | 4931826.768
164.164 | 199.851 | 203.93 | 4563444.538
142.567 | 173.56 | 177.102 | 3963102.291
102.791 | 125.136 | 127.69 | 2857386.743
54.571 | 66.434 | 67.79 | 1516969.727
10.253 | 12.482 | 12.737 | 285017.082
0.319 | 0.389 | 0.397 | 8878.628
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.23 | 11.237 | 11.466 | 256583.424
50.441 | 61.406 | 62.66 | 1402163.163
98.574 | 120.003 | 122.453 | 2740177.413
138.098 | 168.119 | 171.55 | 3838864.632
162.872 | 198.279 | 202.326 | 4527544.01
174.034 | 211.867 | 216.191 | 4837817.079
172.348 | 209.815 | 214.097 | 4790957.451
160.43 | 195.306 | 199.292 | 4459657.334
137.027 | 166.816 | 170.22 | 3809104.633
102.731 | 125.063 | 127.616 | 2855721.717
59.88 | 72.897 | 74.385 | 1664548.431
21.714 | 26.434 | 26.973 | 603599.921
6.246 | 7.604 | 7.759 | 173629.339
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.175 | 14.821 | 15.124 | 338432.685
52.749 | 64.216 | 65.526 | 1466319.701
98.596 | 120.03 | 122.48 | 2740790.14
122.461 | 149.082 | 152.125 | 3404176.366
142.072 | 172.957 | 176.487 | 3949337.097
163.982 | 199.63 | 203.704 | 4558392.442
157.469 | 191.701 | 195.614 | 4377344.485
142.525 | 173.509 | 177.05 | 3961937.097
121.187 | 147.532 | 150.543 | 3368775.67
90.182 | 109.787 | 112.028 | 2506898.79
48.534 | 59.085 | 60.291 | 1349158.623
10.998 | 13.389 | 13.662 | 305725.188
3.02 | 3.676 | 3.751 | 83941.741
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.264 | 14.93 | 15.235 | 340916.485
57.484 | 69.981 | 71.409 | 1597956.235
103.687 | 126.228 | 128.804 | 2882312.701
137.203 | 167.03 | 170.439 | 3813995.582
152.103 | 185.168 | 188.947 | 4228168.75
157.019 | 191.154 | 195.055 | 4364845.262
154.04 | 187.527 | 191.354 | 4282028.198
141.8 | 172.626 | 176.149 | 3941777.075
120.4 | 146.574 | 149.565 | 3346897.987
90.611 | 110.309 | 112.56 | 2518817.037
48.279 | 58.774 | 59.974 | 1342062.299
11.116 | 13.533 | 13.809 | 309011.371
3.337 | 4.062 | 4.145 | 92755.726
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.682 | 15.439 | 15.754 | 352536.564
61.276 | 74.597 | 76.12 | 1703364.596
104.903 | 127.709 | 130.315 | 2916125.022
139.937 | 170.359 | 173.835 | 3890002.372
154.172 | 187.687 | 191.518 | 4285689.31
158.982 | 193.543 | 197.493 | 4419401.933
153.979 | 187.453 | 191.278 | 4280334.663
141.82 | 172.65 | 176.173 | 3942325.159
120.143 | 146.261 | 149.246 | 3339753.411
90.576 | 110.267 | 112.517 | 2517853.507
49.585 | 60.365 | 61.597 | 1378382.546
11.773 | 14.332 | 14.625 | 327264.186
3.659 | 4.455 | 4.546 | 101723.123
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.24 | 11.248 | 11.478 | 256845.458
53.112 | 64.658 | 65.978 | 1476416.158
75.489 | 91.899 | 93.775 | 2098446.432
109.99 | 133.901 | 136.634 | 3057522.68
130.776 | 159.206 | 162.455 | 3635338.273
150.199 | 182.851 | 186.583 | 4175257.362
156.175 | 190.126 | 194.006 | 4341374.931
147.805 | 179.936 | 183.608 | 4108697.027
128.108 | 155.957 | 159.14 | 3561157.656
93.671 | 114.034 | 116.361 | 2603875.72
47.42 | 57.728 | 58.906 | 1318176.522
21.852 | 26.602 | 27.145 | 607438.571
4.802 | 5.845 | 5.965 | 133474.825
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
16.494 | 20.079 | 20.489 | 458493.009
43.777 | 53.294 | 54.381 | 1216921.37
91.298 | 111.145 | 113.414 | 2537912.752
115.646 | 140.786 | 143.659 | 3214737.495
45.268 | 55.109 | 56.234 | 1258370.474
149.742 | 182.295 | 186.015 | 4162556.475
156.375 | 190.37 | 194.255 | 4346943.25
138.416 | 168.507 | 171.946 | 3847719.134
111.593 | 135.852 | 138.625 | 3102076.046
53.648 | 65.31 | 66.643 | 1491306.029
40.782 | 49.648 | 50.661 | 1133669.117
22.135 | 26.947 | 27.497 | 615313.152
6.471 | 7.878 | 8.039 | 179887.146
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.846 | 19.29 | 19.684 | 440478.102
50.289 | 61.221 | 62.47 | 1397933.193
96.778 | 117.817 | 120.222 | 2690257.392
129.241 | 157.337 | 160.548 | 3592663.715
151.015 | 183.844 | 187.596 | 4197933.045
160.146 | 194.96 | 198.939 | 4451758.627
147.714 | 179.826 | 183.496 | 4106181.366
142.841 | 173.894 | 177.443 | 3970726.956
122.774 | 149.464 | 152.514 | 3412889.464
90.271 | 109.895 | 112.138 | 2509366.199
47.625 | 57.979 | 59.162 | 1323898.253
14.864 | 18.096 | 18.465 | 413201.903
5.151 | 6.271 | 6.399 | 143191.97
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.054 | 13.458 | 13.732 | 307293.71
51.054 | 62.153 | 63.422 | 1419214.54
98.603 | 120.038 | 122.488 | 2740975.413
130.799 | 159.234 | 162.484 | 3635979.509
146.279 | 178.079 | 181.713 | 4066288.776
147.757 | 179.879 | 183.55 | 4107387.077
154.925 | 188.605 | 192.454 | 4306639.597
144.438 | 175.837 | 179.426 | 4015102.784
122.262 | 148.841 | 151.878 | 3398660.572
86.172 | 104.905 | 107.046 | 2395422.278
27.873 | 33.933 | 34.625 | 774826.494
9.598 | 11.685 | 11.923 | 266812.519
3.128 | 3.808 | 3.886 | 86953.882
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.423 | 13.906 | 14.19 | 317534.923
54.826 | 66.745 | 68.107 | 1524066.051
102.9 | 125.269 | 127.826 | 2860423.01
140.096 | 170.552 | 174.032 | 3894413.232
161.937 | 197.14 | 201.164 | 4501541.627
167.9 | 204.4 | 208.572 | 4667312.776
162.407 | 197.713 | 201.748 | 4514617.333
147.276 | 179.292 | 182.951 | 4093992.429
125.975 | 153.36 | 156.49 | 3501859.175
95.937 | 116.793 | 119.176 | 2666871.447
53.992 | 65.73 | 67.071 | 1500886.153
15.988 | 19.463 | 19.861 | 444429.647
5.787 | 7.045 | 7.189 | 160868.192
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.263 | 17.363 | 17.718 | 396477.203
61.558 | 74.941 | 76.47 | 1711210.668
108.975 | 132.666 | 135.373 | 3029314.812
141.828 | 172.66 | 176.184 | 3942555.332
155.271 | 189.026 | 192.884 | 4316255.965
154.417 | 187.986 | 191.823 | 4292511.592
154.103 | 187.604 | 191.433 | 4283786.376
144.681 | 176.133 | 179.728 | 4021860.423
123.487 | 150.332 | 153.4 | 3432710.801
94.159 | 114.629 | 116.968 | 2617455.641
54.898 | 66.832 | 68.196 | 1526057.754
14.638 | 17.82 | 18.184 | 406907.962
4.813 | 5.859 | 5.979 | 133789.384
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.053 | 13.455 | 13.73 | 307241.185
50.586 | 61.583 | 62.84 | 1406199.094
93.803 | 114.195 | 116.526 | 2607553.223
130.15 | 158.443 | 161.677 | 3617924.085
151.473 | 184.402 | 188.165 | 4210670.066
170.808 | 207.94 | 212.184 | 4748145.872
127.208 | 154.861 | 158.022 | 3536135.194
135.503 | 164.96 | 168.327 | 3766732.626
123.158 | 149.932 | 152.991 | 3423570.139
78.934 | 96.093 | 98.054 | 2194209.916
32.492 | 39.555 | 40.363 | 903213.089
13.621 | 16.582 | 16.92 | 378635.451
5.334 | 6.494 | 6.626 | 148280.2
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.936 | 12.096 | 12.343 | 276203.097
49.128 | 59.808 | 61.028 | 1365665.268
92.583 | 112.71 | 115.01 | 2573640.015
127.54 | 155.266 | 158.434 | 3545372.25
150.012 | 182.624 | 186.351 | 4170068.245
164.165 | 199.853 | 203.932 | 4563485.055
161.223 | 196.271 | 200.277 | 4481696.164
145.164 | 176.722 | 180.328 | 4035298.94
122.98 | 149.715 | 152.77 | 3418618.93
57.35 | 69.818 | 71.243 | 1594234.863
26.093 | 31.765 | 32.413 | 725329.654
21.401 | 26.054 | 26.586 | 594919.605
8.077 | 9.833 | 10.034 | 224529.281
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
7.307 | 8.895 | 9.077 | 203115.296
31.165 | 37.941 | 38.715 | 866344.648
47.283 | 57.562 | 58.737 | 1314382.772
39.117 | 47.621 | 48.593 | 1087386.082
123.183 | 149.962 | 153.023 | 3424264.01
160.14 | 194.954 | 198.932 | 4451609.488
149.561 | 182.074 | 185.79 | 4157516.497
121.719 | 148.18 | 151.204 | 3383569.037
94.845 | 115.463 | 117.819 | 2636506.456
73.315 | 89.253 | 91.074 | 2038018.891
45.06 | 54.856 | 55.975 | 1252588.373
19.511 | 23.753 | 24.238 | 542378.763
5.869 | 7.145 | 7.291 | 163150.328
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.098 | 15.945 | 16.271 | 364096.383
59.097 | 71.945 | 73.413 | 1642800.034
107.401 | 130.749 | 133.417 | 2985547.438
143.411 | 174.587 | 178.15 | 3986556.231
160.764 | 195.713 | 199.707 | 4468947.025
164.468 | 200.222 | 204.309 | 4571912.103
159.511 | 194.187 | 198.15 | 4434106.531
143.918 | 175.204 | 178.78 | 4000648.102
126.125 | 153.544 | 156.677 | 3506048.518
95.727 | 116.538 | 118.916 | 2661045.477
54.177 | 65.955 | 67.301 | 1506027.018
15.877 | 19.329 | 19.723 | 441357.136
6.368 | 7.752 | 7.911 | 177016.409
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
4.934 | 6.007 | 6.129 | 137159.953
22.506 | 27.399 | 27.958 | 625631.016
39.688 | 48.316 | 49.302 | 1103255.874
48.73 | 59.323 | 60.534 | 1354597.656
70.291 | 85.572 | 87.318 | 1953964.255
129.948 | 158.197 | 161.426 | 3612307.514
114.392 | 139.26 | 142.102 | 3179889.266
78.607 | 95.695 | 97.648 | 2185121.889
92.915 | 113.114 | 115.423 | 2582869.446
89.617 | 109.099 | 111.325 | 2491185.762
61.459 | 74.82 | 76.347 | 1708452.826
23.942 | 29.146 | 29.741 | 665531.341
10.39 | 12.649 | 12.907 | 288827.223
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
4.294 | 5.228 | 5.334 | 119370.836
39.963 | 48.651 | 49.644 | 1110904.665
89.685 | 109.181 | 111.409 | 2493064.57
124.475 | 151.535 | 154.628 | 3460180.929
146.619 | 178.493 | 182.136 | 4075743.997
119.633 | 145.64 | 148.612 | 3325572.771
103.08 | 125.489 | 128.05 | 2865438.862
45.626 | 55.545 | 56.679 | 1268325.527
24.636 | 29.992 | 30.604 | 684840.728
33.935 | 41.313 | 42.156 | 943343.477
22.341 | 27.197 | 27.752 | 621026.227
7.562 | 9.206 | 9.394 | 210211.62
1.058 | 1.288 | 1.314 | 29409.196
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
6.365 | 7.749 | 7.907 | 176939.648
30.151 | 36.705 | 37.454 | 838132.507
70.411 | 85.718 | 87.467 | 1957298.69
100.082 | 121.839 | 124.326 | 2782097.84
84.073 | 102.349 | 104.438 | 2337063.201
146.119 | 177.884 | 181.515 | 4061841.782
161.619 | 196.753 | 200.768 | 4492699.133
136.478 | 166.147 | 169.538 | 3793835.56
83.275 | 101.378 | 103.447 | 2314887.35
62.673 | 76.298 | 77.855 | 1742200.504
42.797 | 52.1 | 53.163 | 1189665.024
19.463 | 23.694 | 24.178 | 541036.031
9.885 | 12.034 | 12.279 | 274783.604
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.259 | 13.707 | 13.986 | 312982.659
49.54 | 60.31 | 61.54 | 1377124.2
92.678 | 112.825 | 115.128 | 2576272.954
126.488 | 153.986 | 157.128 | 3516140.592
143.941 | 175.232 | 178.808 | 4001284.955
130.421 | 158.773 | 162.014 | 3625459.981
121.735 | 148.199 | 151.224 | 3384008.609
130.465 | 158.827 | 162.068 | 3626685.435
126.326 | 153.789 | 156.927 | 3511640.963
95.162 | 115.849 | 118.214 | 2645324.824
57.987 | 70.592 | 72.033 | 1611918.82
20.571 | 25.043 | 25.554 | 571836.211
8.113 | 9.877 | 10.079 | 225533.328
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.657 | 14.192 | 14.481 | 324054.654
52.282 | 63.648 | 64.946 | 1453344.772
96.675 | 117.691 | 120.093 | 2687382.272
133.109 | 162.046 | 165.353 | 3700188.682
155.435 | 189.225 | 193.086 | 4320799.463
167.116 | 203.445 | 207.597 | 4645507.471
166.897 | 203.179 | 207.326 | 4639431.585
152.578 | 185.748 | 189.538 | 4241397.868
131.011 | 159.492 | 162.747 | 3641870.122
97.245 | 118.385 | 120.801 | 2703227.938
55.501 | 67.567 | 68.946 | 1542835.089
18.905 | 23.015 | 23.484 | 525524.667
7.889 | 9.604 | 9.8 | 219299.647
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.502 | 17.655 | 18.015 | 403133.955
58.693 | 71.453 | 72.911 | 1631566.892
104.543 | 127.27 | 129.868 | 2906109.709
139.693 | 170.061 | 173.531 | 3883204.216
159.804 | 194.543 | 198.514 | 4442243.146
166.389 | 202.561 | 206.695 | 4625315.588
159.574 | 194.263 | 198.228 | 4435848.318
145.607 | 177.26 | 180.878 | 4047596.499
124.308 | 151.331 | 154.42 | 3455527.888
92.872 | 113.061 | 115.369 | 2581663.735
53.421 | 65.035 | 66.362 | 1485016.361
16.959 | 20.646 | 21.067 | 471431.694
7.392 | 8.998 | 9.182 | 205469.81
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.884 | 18.119 | 18.489 | 413737.979
58.684 | 71.441 | 72.899 | 1631300.585
105.762 | 128.754 | 131.381 | 2939990.025
139.168 | 169.422 | 172.88 | 3868616.896
157.873 | 192.194 | 196.116 | 4388589.635
166.838 | 203.107 | 207.252 | 4637786.302
160.726 | 195.666 | 199.659 | 4467878.335
146.022 | 177.766 | 181.394 | 4059144.2
123.349 | 150.164 | 153.229 | 3428876.534
94.048 | 114.494 | 116.83 | 2614371.122
53.256 | 64.833 | 66.156 | 1480411.572
16.206 | 19.729 | 20.132 | 450497.798
7.104 | 8.649 | 8.825 | 197486.607
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.558 | 16.506 | 16.843 | 376898.047
55.561 | 67.639 | 69.02 | 1544488.107
99.652 | 121.315 | 123.791 | 2770134.693
134.649 | 163.92 | 167.266 | 3742988.253
155.6 | 189.425 | 193.291 | 4325375.853
164.367 | 200.099 | 204.182 | 4569097.243
159.657 | 194.365 | 198.332 | 4438170.971
147.532 | 179.604 | 183.269 | 4101112.879
125.889 | 153.257 | 156.384 | 3499492.543
92.626 | 112.762 | 115.063 | 2574829.335
51.63 | 62.854 | 64.137 | 1435221.353
17.613 | 21.442 | 21.879 | 489607.748
7.598 | 9.25 | 9.439 | 211215.667
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.801 | 15.584 | 15.902 | 355846.873
53 | 64.522 | 65.839 | 1473307.513
97.231 | 118.369 | 120.784 | 2702853.009
130.921 | 159.382 | 162.635 | 3639362.196
152.312 | 185.424 | 189.208 | 4234003.376
160.903 | 195.882 | 199.88 | 4472809.801
149.165 | 181.593 | 185.299 | 4146525.536
135.964 | 165.522 | 168.9 | 3779558.416
74.557 | 90.765 | 92.617 | 2072544.826
49.008 | 59.662 | 60.88 | 1362335.216
32.138 | 39.125 | 39.923 | 893382.939
14.155 | 17.232 | 17.583 | 393477.07
2.826 | 3.44 | 3.51 | 78550.96
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.402 | 17.533 | 17.89 | 400347.604
44.57 | 54.26 | 55.367 | 1238976.591
89.073 | 108.437 | 110.65 | 2476070.101
124.992 | 152.164 | 155.269 | 3474542.459
149.654 | 182.187 | 185.905 | 4160096.801
160.455 | 195.337 | 199.323 | 4460358.83
158.223 | 192.62 | 196.551 | 4398318.898
144.646 | 176.09 | 179.684 | 4020880.502
123.435 | 150.268 | 153.335 | 3431255.174
93.769 | 114.154 | 116.484 | 2606613.819
52.179 | 63.522 | 64.819 | 1450478.418
22.059 | 26.855 | 27.403 | 613208.554
5.339 | 6.5 | 6.632 | 148417.221
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.263 | 13.711 | 13.991 | 313083.546
34.61 | 42.134 | 42.994 | 962096.124
68.235 | 83.068 | 84.764 | 1896798.881
119.549 | 145.538 | 148.508 | 3323242.383
125.979 | 153.365 | 156.495 | 3501972.07
142.466 | 173.437 | 176.976 | 3960291.814
152.506 | 185.659 | 189.448 | 4239377.766
134.953 | 164.29 | 167.643 | 3751435.044
116.016 | 141.237 | 144.12 | 3225035.616
91.946 | 111.934 | 114.219 | 2555927.659
56.02 | 68.198 | 69.59 | 1557249.254
19.483 | 23.719 | 24.203 | 541600.506
4.865 | 5.923 | 6.044 | 135245.011
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.512 | 16.449 | 16.785 | 375603.567
56.831 | 69.186 | 70.598 | 1579804.307
80.068 | 97.474 | 99.463 | 2225740.101
117.144 | 142.611 | 145.521 | 3256400.271
123.247 | 150.039 | 153.101 | 3426025.54
113.024 | 137.594 | 140.402 | 3141851.358
149.532 | 182.039 | 185.755 | 4156718.497
150.459 | 183.167 | 186.906 | 4182478.699
118.864 | 144.704 | 147.657 | 3304199.303
95.693 | 116.496 | 118.873 | 2660089.682
53.898 | 65.615 | 66.954 | 1498265.332
20.724 | 25.23 | 25.745 | 576102.315
6.093 | 7.417 | 7.569 | 169367.618
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.215 | 16.087 | 16.416 | 367342.049
53.495 | 65.124 | 66.453 | 1487056.316
99.297 | 120.883 | 123.35 | 2760268.409
133.718 | 162.787 | 166.11 | 3717115.156
159.916 | 194.68 | 198.653 | 4445363.799
170.361 | 207.395 | 211.628 | 4735707.019
169.155 | 205.928 | 210.131 | 4702201.522
155.162 | 188.893 | 192.748 | 4313219.698
131.062 | 159.554 | 162.81 | 3643285.232
96.388 | 117.341 | 119.736 | 2679394.796
55.683 | 67.788 | 69.172 | 1547887.185
17.706 | 21.555 | 21.995 | 492192.435
5.192 | 6.32 | 6.449 | 144316.647
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
17.596 | 21.421 | 21.859 | 489136.425
62.551 | 76.149 | 77.703 | 1738801.426
108.237 | 131.766 | 134.456 | 3008779.971
143.397 | 174.57 | 178.133 | 3986169.294
164.148 | 199.832 | 203.91 | 4563004.966
170.498 | 207.563 | 211.798 | 4739529.168
168.363 | 204.964 | 209.147 | 4680186.818
156.13 | 190.071 | 193.95 | 4340120.968
135.474 | 164.925 | 168.291 | 3765930.243
99.547 | 121.187 | 123.66 | 2767211.321
58.232 | 70.891 | 72.337 | 1618736.719
22.323 | 27.175 | 27.73 | 620526.395
5.22 | 6.355 | 6.484 | 145106.912
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
16.55 | 20.148 | 20.559 | 460061.531
60.325 | 73.439 | 74.938 | 1676922.641
98.347 | 119.726 | 122.17 | 2733854.963
136.636 | 166.339 | 169.734 | 3798222.294
154.416 | 187.985 | 191.821 | 4292483.083
173.974 | 211.794 | 216.117 | 4836152.053
162.756 | 198.138 | 202.182 | 4524322.47
149.969 | 182.571 | 186.297 | 4168862.534
91.796 | 111.751 | 114.032 | 2551750.324
1.157 | 1.408 | 1.437 | 32155.03
7.266 | 8.846 | 9.027 | 201990.619
16.441 | 20.016 | 20.424 | 457041.655
5.48 | 6.672 | 6.808 | 152344.64
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.054 | 17.109 | 17.459 | 390675.359
54.726 | 66.623 | 67.982 | 1521279.7
100.667 | 122.551 | 125.052 | 2798354.569
137.041 | 166.832 | 170.237 | 3809479.562
159.944 | 194.715 | 198.688 | 4446154.064
168.135 | 204.686 | 208.863 | 4673840.242
166.175 | 202.299 | 206.428 | 4619343.941
153.738 | 187.16 | 190.979 | 4273641.667
129.018 | 157.066 | 160.271 | 3586470.551
95.019 | 115.675 | 118.036 | 2641349.153
54.727 | 66.624 | 67.983 | 1521303.826
19.268 | 23.456 | 23.935 | 535604.733
6.189 | 7.535 | 7.689 | 172053.082
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.01 | 17.055 | 17.403 | 389441.139
51.405 | 62.58 | 63.857 | 1428963.546
94.557 | 115.113 | 117.463 | 2628515.628
128.547 | 156.492 | 159.686 | 3573370.719
150.705 | 183.467 | 187.211 | 4189320.724
160.692 | 195.626 | 199.618 | 4466955.322
160.476 | 195.362 | 199.349 | 4460935.423
149.031 | 181.429 | 185.132 | 4142787.773
125.018 | 152.195 | 155.301 | 3475256.073
93.506 | 113.833 | 116.157 | 2599291.705
55.252 | 67.263 | 68.636 | 1535899.912
20.199 | 24.59 | 25.092 | 561494.221
5.795 | 7.055 | 7.199 | 161093.982
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.939 | 16.97 | 17.316 | 387489.953
52.924 | 64.429 | 65.744 | 1471186.524
95.368 | 116.1 | 118.47 | 2651054.29
128.706 | 156.685 | 159.883 | 3577781.579
151.442 | 184.364 | 188.127 | 4209807.423
163.388 | 198.907 | 202.967 | 4541885.797
161.668 | 196.813 | 200.83 | 4494070.374
148.927 | 181.303 | 185.003 | 4139904.918
126.134 | 153.555 | 156.688 | 3506298.434
93.99 | 114.423 | 116.758 | 2612754.348
54.431 | 66.264 | 67.616 | 1513082.825
20.893 | 25.435 | 25.954 | 580787.217
6.378 | 7.764 | 7.922 | 177286.068
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.356 | 10.172 | 10.38 | 232274.576
58.705 | 71.467 | 72.926 | 1631893.569
87.925 | 107.039 | 109.223 | 2444148.596
133.085 | 162.016 | 165.323 | 3699511.312
153.262 | 186.58 | 190.387 | 4260400.431
159.552 | 194.237 | 198.201 | 4435247.599
158.154 | 192.536 | 196.465 | 4396399.573
146.157 | 177.93 | 181.561 | 4062889.698
125.929 | 153.305 | 156.434 | 3500597.477
95.892 | 116.738 | 119.121 | 2665621.867
52.69 | 64.144 | 65.453 | 1464678.801
24.716 | 30.089 | 30.703 | 687058.221
7.16 | 8.716 | 8.894 | 199026.73
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.47 | 16.398 | 16.733 | 374438.373
52.035 | 63.347 | 64.639 | 1446474.238
95.605 | 116.389 | 118.764 | 2657646.399
128.253 | 156.134 | 159.32 | 3565193.587
147.501 | 179.566 | 183.231 | 4100250.236
152.712 | 185.91 | 189.704 | 4245107.232
151.992 | 185.033 | 188.81 | 4225088.614
147.519 | 179.588 | 183.253 | 4100750.068
115.587 | 140.714 | 143.586 | 3213096.595
71.414 | 86.938 | 88.713 | 1985167.873
48.307 | 58.808 | 60.008 | 1342836.173
18.786 | 22.87 | 23.337 | 522218.741
6.403 | 7.795 | 7.954 | 177991.947
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.368 | 17.491 | 17.848 | 399396.192
54.528 | 66.382 | 67.737 | 1515780.407
95.182 | 115.873 | 118.238 | 2645872.908
127.242 | 154.904 | 158.065 | 3537102.997
144.828 | 176.312 | 179.91 | 4025944.606
152.525 | 185.682 | 189.471 | 4239901.724
149.703 | 182.247 | 185.967 | 4161468.042
135.97 | 165.529 | 168.907 | 3779719.563
119.981 | 146.063 | 149.044 | 3335237.391
88.267 | 107.455 | 109.648 | 2453652.069
53.037 | 64.567 | 65.885 | 1474335.686
19.098 | 23.25 | 23.724 | 530891.322
6.09 | 7.414 | 7.565 | 169290.857
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.004 | 18.266 | 18.639 | 417088.805
52.988 | 64.507 | 65.824 | 1472968.828
91.12 | 110.929 | 113.193 | 2532973.551
116.691 | 142.059 | 144.958 | 3243800.271
133.644 | 162.697 | 166.017 | 3715054.427
138.381 | 168.464 | 171.902 | 3846739.213
136.531 | 166.211 | 169.604 | 3795303.305
127.28 | 154.949 | 158.111 | 3538138.905
110.817 | 134.908 | 137.661 | 3080512.922
85.023 | 103.507 | 105.619 | 2363493.038
48.736 | 59.33 | 60.541 | 1354758.803
20.73 | 25.237 | 25.752 | 576263.462
7.137 | 8.689 | 8.866 | 198401.885
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.474 | 17.62 | 17.98 | 402343.69
53.198 | 64.762 | 66.084 | 1478794.798
94.121 | 114.582 | 116.921 | 2616391.334
120.096 | 146.204 | 149.187 | 3338446.813
147.445 | 179.498 | 183.161 | 4098693.722
159.592 | 194.286 | 198.251 | 4436364.541
156.648 | 190.701 | 194.593 | 4354511.007
147.311 | 179.335 | 182.995 | 4094972.35
124.042 | 151.008 | 154.089 | 3448141.021
93.811 | 114.205 | 116.536 | 2607779.013
52.228 | 63.582 | 64.879 | 1451840.893
23.099 | 28.121 | 28.695 | 642117.918
5.659 | 6.889 | 7.029 | 157303.584
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.678 | 16.651 | 16.991 | 380216.091
49.288 | 60.003 | 61.228 | 1370121.028
90.808 | 110.549 | 112.805 | 2524296.587
106.808 | 130.027 | 132.681 | 2969064.919
147.39 | 179.432 | 183.094 | 4097182.108
146.769 | 178.675 | 182.322 | 4079904.941
130.153 | 158.447 | 161.681 | 3618012.854
126.312 | 153.771 | 156.91 | 3511242.018
102.56 | 124.856 | 127.404 | 2850984.18
78.584 | 95.667 | 97.619 | 2184480.653
53.771 | 65.461 | 66.797 | 1494745.624
24.824 | 30.22 | 30.837 | 690053.971
6.401 | 7.792 | 7.951 | 177927.304
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.125 | 14.761 | 15.062 | 337053.709
51.687 | 62.924 | 64.208 | 1436814.001
87.323 | 106.307 | 108.476 | 2427428.169
120.542 | 146.747 | 149.742 | 3350849.532
144.213 | 175.564 | 179.147 | 4008861.368
152.159 | 185.236 | 189.017 | 4229725.264
156.446 | 190.456 | 194.343 | 4348910.827
147.805 | 179.937 | 183.609 | 4108713.418
127.019 | 154.632 | 157.787 | 3530893.442
69.302 | 84.368 | 86.089 | 1926470.001
27.471 | 33.442 | 34.125 | 763629.596
17.486 | 21.287 | 21.722 | 486076.032
6.419 | 7.815 | 7.975 | 178447.91
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
20.028 | 24.382 | 24.879 | 556740.293
62.943 | 76.627 | 78.19 | 1749707.891
100.182 | 121.961 | 124.45 | 2784879.808
123.036 | 149.783 | 152.839 | 3420171.061
136.135 | 165.73 | 169.112 | 3784307.961
141.603 | 172.386 | 175.904 | 3936297.525
138.834 | 169.015 | 172.465 | 3859327.205
126.913 | 154.503 | 157.656 | 3527950.327
111.614 | 135.878 | 138.651 | 3102664.647
84.177 | 102.477 | 104.568 | 2339974.455
47.953 | 58.377 | 59.568 | 1332994.015
14.942 | 18.19 | 18.561 | 415354.753
4.957 | 6.035 | 6.158 | 137801.189
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
17.022 | 20.723 | 21.145 | 473185.489
59.039 | 71.873 | 73.34 | 1641166.869
97.153 | 118.273 | 120.686 | 2700667.377
123.953 | 150.9 | 153.979 | 3445673.612
135.974 | 165.533 | 168.912 | 3779820.45
144.326 | 175.702 | 179.287 | 4012006.147
141.99 | 172.857 | 176.385 | 3947054.961
130.93 | 159.394 | 162.646 | 3639624.12
113.289 | 137.917 | 140.731 | 3149221.724
87.389 | 106.387 | 108.558 | 2429258.725
48.261 | 58.752 | 59.952 | 1341562.467
14.75 | 17.957 | 18.323 | 410028.615
4.52 | 5.502 | 5.614 | 125636.378
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.391 | 16.302 | 16.635 | 372245.006
52.975 | 64.492 | 65.808 | 1472618.025
94.085 | 114.538 | 116.876 | 2615387.287
127.857 | 155.652 | 158.829 | 3554190.618
145.314 | 176.904 | 180.514 | 4039459.884
154.257 | 187.792 | 191.624 | 4288072.223
152.158 | 185.236 | 189.017 | 4229717.529
139.159 | 169.411 | 172.869 | 3868366.98
114.878 | 139.851 | 142.705 | 3193388.153
86.683 | 105.527 | 107.681 | 2409627.044
47.752 | 58.133 | 59.32 | 1327422.344
14.632 | 17.812 | 18.176 | 406730.424
4.818 | 5.865 | 5.985 | 133926.405
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
19.271 | 23.461 | 23.94 | 535709.893
62.156 | 75.668 | 77.212 | 1727818.2
102.14 | 124.344 | 126.882 | 2839299.458
130.432 | 158.786 | 162.027 | 3625758.149
142.063 | 172.946 | 176.475 | 3949082.798
146.714 | 178.608 | 182.253 | 4078372.553
143.646 | 174.874 | 178.443 | 3993104.471
135.471 | 164.922 | 168.287 | 3765853.482
117.84 | 143.457 | 146.385 | 3275729.511
89.715 | 109.218 | 111.447 | 2493907.47
49.851 | 60.688 | 61.927 | 1385765.03
15.83 | 19.271 | 19.664 | 440038.53
4.849 | 5.903 | 6.024 | 134793.431
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
23.431 | 28.525 | 29.107 | 651342.966
70.598 | 85.945 | 87.699 | 1962487.807
106.886 | 130.122 | 132.778 | 2971234.16
130.399 | 158.747 | 161.987 | 3624859.262
143 | 174.087 | 177.64 | 3975137.816
146.646 | 178.526 | 182.169 | 4076493.745
143.617 | 174.838 | 178.407 | 3992290.08
131.335 | 159.886 | 163.148 | 3650864.997
112.536 | 137 | 139.796 | 3128287.828
86.219 | 104.962 | 107.104 | 2396724.493
52.147 | 63.483 | 64.779 | 1449587.266
15.541 | 18.919 | 19.305 | 432002.802
4.585 | 5.581 | 5.695 | 127442.808
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
20.851 | 25.384 | 25.902 | 579622.023
63.325 | 77.091 | 78.665 | 1760316.298
101.286 | 123.305 | 125.821 | 2815567.093
129.673 | 157.863 | 161.085 | 3604675.114
142.129 | 173.027 | 176.558 | 3950929.745
145.309 | 176.898 | 180.508 | 4039322.863
141.082 | 171.752 | 175.258 | 3921823.1
130.012 | 158.275 | 161.505 | 3614085.435
111.472 | 135.705 | 138.475 | 3098717.485
86.191 | 104.928 | 107.07 | 2395950.619
53.233 | 64.806 | 66.128 | 1479786.727
15.895 | 19.351 | 19.746 | 441861.351
4.938 | 6.011 | 6.134 | 137260.84
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
18.388 | 22.385 | 22.842 | 511146.746
56.687 | 69.01 | 70.419 | 1575792.502
94.247 | 114.736 | 117.077 | 2619898.924
126.459 | 153.95 | 157.091 | 3515321.818
142.831 | 173.882 | 177.43 | 3970448.531
147.369 | 179.405 | 183.067 | 4096577.116
145.621 | 177.278 | 180.896 | 4047999.827
133.408 | 162.409 | 165.724 | 3708486.444
114.968 | 139.961 | 142.817 | 3195896.079
87.492 | 106.512 | 108.686 | 2432117.454
53.071 | 64.609 | 65.927 | 1475287.098
16.839 | 20.499 | 20.917 | 468080.868
5.005 | 6.092 | 6.217 | 139115.522
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.951 | 19.418 | 19.815 | 443401.474
54.781 | 66.689 | 68.051 | 1522800.08
94.498 | 115.041 | 117.389 | 2626870.345
126.191 | 153.624 | 156.759 | 3507879.074
144.818 | 176.301 | 179.898 | 4025682.572
152.739 | 185.944 | 189.738 | 4245873.371
152.126 | 185.197 | 188.977 | 4228826.377
140.143 | 170.609 | 174.091 | 3895719.83
118.692 | 144.494 | 147.443 | 3299409.241
88.044 | 107.184 | 109.371 | 2447458.905
50.998 | 62.084 | 63.352 | 1417646.018
18.932 | 23.047 | 23.518 | 526266.79
6.407 | 7.8 | 7.959 | 178104.842
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.707 | 17.904 | 18.269 | 408822.904
48.255 | 58.745 | 59.944 | 1341396.937
94.949 | 115.59 | 117.949 | 2639405.702
128.166 | 156.028 | 159.212 | 3562774.43
149.599 | 182.12 | 185.837 | 4158568.796
158.182 | 192.569 | 196.499 | 4397161.439
154.575 | 188.178 | 192.019 | 4296898.326
143.985 | 175.287 | 178.864 | 4002531.183
122.82 | 149.52 | 152.571 | 3414167.553
91.395 | 111.264 | 113.535 | 2540622.342
52.341 | 63.72 | 65.02 | 1454990.055
16.881 | 20.551 | 20.971 | 469266.836
5.616 | 6.837 | 6.976 | 156114.264
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
16.748 | 20.389 | 20.805 | 465565.207
55.233 | 67.24 | 68.613 | 1535375.954
99.637 | 121.297 | 123.772 | 2769719.247
133.713 | 162.781 | 166.103 | 3716973.752
149.966 | 182.567 | 186.293 | 4168773.765
154.879 | 188.548 | 192.396 | 4305345.117
151.548 | 184.493 | 188.258 | 4212750.538
139.839 | 170.238 | 173.713 | 3887256.648
120.328 | 146.487 | 149.476 | 3344906.284
91.382 | 111.247 | 113.517 | 2540238.757
52.167 | 63.508 | 64.804 | 1450151.741
16.333 | 19.884 | 20.29 | 454033.897
4.966 | 6.045 | 6.169 | 138039.097
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
19.918 | 24.248 | 24.743 | 553684.283
59.668 | 72.639 | 74.122 | 1658657.818
104.487 | 127.202 | 129.798 | 2904553.195
128.655 | 156.623 | 159.82 | 3576366.469
141.762 | 172.58 | 176.102 | 3940724.776
145.11 | 176.656 | 180.261 | 4033795.061
143.076 | 174.179 | 177.734 | 3977242.414
133.724 | 162.795 | 166.117 | 3717288.311
114.251 | 139.088 | 141.927 | 3175966.23
86.736 | 105.591 | 107.746 | 2411090.406
51.735 | 62.982 | 64.267 | 1438140.342
14.727 | 17.929 | 18.295 | 409391.762
4.43 | 5.393 | 5.503 | 123144.843
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
18.521 | 22.547 | 23.007 | 514843.992
57.241 | 69.685 | 71.107 | 1591198.596
103.667 | 126.204 | 128.779 | 2881760.234
130.694 | 159.106 | 162.353 | 3633056.137
144.509 | 175.924 | 179.514 | 4017082.369
149.342 | 181.807 | 185.518 | 4151424.22
145.107 | 176.652 | 180.257 | 4033706.292
134.463 | 163.694 | 167.034 | 3737818.879
114.768 | 139.718 | 142.569 | 3190344.151
87.408 | 106.409 | 108.581 | 2429770.675
52.559 | 63.985 | 65.291 | 1461046.198
15.721 | 19.139 | 19.529 | 437018.654
4.703 | 5.726 | 5.842 | 130740.999
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
17.54 | 21.353 | 21.789 | 487579.911
58.857 | 71.653 | 73.115 | 1636131.164
103.015 | 125.41 | 127.969 | 2863632.432
128.917 | 156.943 | 160.146 | 3583664.457
141.369 | 172.101 | 175.614 | 3929794.185
145.708 | 177.384 | 181.004 | 4050418.984
142.028 | 172.903 | 176.432 | 3948107.26
131.728 | 160.365 | 163.638 | 3661804.354
112.875 | 137.413 | 140.217 | 3137714.54
86.112 | 104.832 | 106.971 | 2393752.869
52.236 | 63.591 | 64.889 | 1452054.675
15.176 | 18.475 | 18.853 | 421866.859
4.21 | 5.126 | 5.23 | 117040.448
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
19.641 | 23.91 | 24.398 | 545970.849
63.073 | 76.784 | 78.351 | 1753304.36
103.367 | 125.838 | 128.406 | 2873409.947
127.418 | 155.118 | 158.284 | 3541993.946
141.423 | 172.167 | 175.68 | 3931293.681
145.879 | 177.591 | 181.216 | 4055156.521
143.773 | 175.028 | 178.6 | 3996624.179
132.256 | 161.007 | 164.293 | 3676468.435
113.119 | 137.71 | 140.521 | 3144500.688
86.465 | 105.262 | 107.41 | 2403570.901
49.455 | 60.206 | 61.435 | 1374757.678
14.786 | 18.001 | 18.368 | 411032.662
4.051 | 4.932 | 5.032 | 112613.197
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.819 | 19.258 | 19.652 | 439744.745
54.31 | 66.116 | 67.465 | 1509707.873
95.514 | 116.278 | 118.651 | 2655114.347
129.358 | 157.479 | 160.693 | 3595909.381
142.854 | 173.909 | 177.459 | 3971077.759
146.565 | 178.426 | 182.068 | 4074223.727
143.917 | 175.203 | 178.778 | 4000619.593
132.835 | 161.712 | 165.012 | 3692564.017
114.235 | 139.069 | 141.907 | 3175526.658
87.768 | 106.848 | 109.028 | 2439785.988
50.688 | 61.707 | 62.966 | 1409029.314
18.84 | 22.936 | 23.404 | 523722.62
6.593 | 8.027 | 8.19 | 183281.841
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.303 | 16.195 | 16.525 | 369797.34
47.607 | 57.957 | 59.14 | 1323398.421
87.085 | 106.017 | 108.18 | 2420807.551
118.231 | 143.933 | 146.87 | 3286595.459
138.822 | 169.001 | 172.45 | 3859000.528
148.264 | 180.495 | 184.178 | 4121458.174
147.516 | 179.585 | 183.25 | 4100677.69
136.993 | 166.774 | 170.177 | 3808148.838
117.026 | 142.466 | 145.374 | 3253102.08
86.973 | 105.881 | 108.041 | 2417698.906
52.214 | 63.565 | 64.862 | 1451453.956
21.075 | 25.656 | 26.18 | 585839.313
7.214 | 8.783 | 8.962 | 200547
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.879 | 18.113 | 18.483 | 413600.958
53.044 | 64.575 | 65.893 | 1474520.959
95.547 | 116.318 | 118.691 | 2656025.242
128.255 | 156.137 | 159.323 | 3565258.23
149.815 | 182.383 | 186.105 | 4164572.304
159.578 | 194.269 | 198.234 | 4435977.604
157.51 | 191.751 | 195.665 | 4378485.553
145.479 | 177.104 | 180.719 | 4044036.274
123.241 | 150.033 | 153.095 | 3425880.784
92.532 | 112.647 | 114.946 | 2572208.514
53.788 | 65.482 | 66.818 | 1495221.33
20.838 | 25.368 | 25.886 | 579259.212
6.474 | 7.881 | 8.042 | 179959.524
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
19.795 | 24.098 | 24.59 | 550261.079
64.806 | 78.895 | 80.505 | 1801498.985
102.828 | 125.182 | 127.737 | 2858431.307
127.02 | 154.633 | 157.789 | 3530921.951
141.182 | 171.874 | 175.382 | 3924605.068
146.859 | 178.785 | 182.433 | 4082408.484
144.686 | 176.139 | 179.734 | 4021997.444
134.634 | 163.902 | 167.247 | 3742572.807
116.496 | 141.821 | 144.715 | 3238368.973
88.75 | 108.043 | 110.248 | 2467078.578
53.257 | 64.834 | 66.158 | 1480440.081
16.375 | 19.935 | 20.342 | 455199.091
4.784 | 5.824 | 5.942 | 132982.618
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
19.761 | 24.056 | 24.547 | 549305.284
64.739 | 78.813 | 80.421 | 1799627.912
104.415 | 127.114 | 129.709 | 2902549.484
133.518 | 162.544 | 165.861 | 3711558.845
147.169 | 179.163 | 182.819 | 4091037.196
153.635 | 187.034 | 190.851 | 4270770.93
151.322 | 184.218 | 187.978 | 4206472.988
141.185 | 171.877 | 175.385 | 3924677.446
122 | 148.522 | 151.553 | 3391378.975
93.429 | 113.74 | 116.061 | 2597158.598
58.042 | 70.66 | 72.102 | 1613463.216
19.264 | 23.452 | 23.931 | 535508.229
5.77 | 7.025 | 7.168 | 160404.494
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
18.83 | 22.923 | 23.391 | 523432.187
61.371 | 74.712 | 76.237 | 1705993.152
104.388 | 127.081 | 129.675 | 2901795.353
133.855 | 162.954 | 166.279 | 3720920.914
146.526 | 178.379 | 182.02 | 4073147.302
151.542 | 184.486 | 188.251 | 4212589.391
149.211 | 181.648 | 185.355 | 4147787.234
136.787 | 166.523 | 169.922 | 3802423.755
118.587 | 144.366 | 147.313 | 3296490.252
90.787 | 110.523 | 112.779 | 2523707.986
55.898 | 68.05 | 69.438 | 1553862.184
18.354 | 22.344 | 22.8 | 510207.342
5.447 | 6.631 | 6.767 | 151417.354
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
20.844 | 25.375 | 25.893 | 579420.359
65.318 | 79.518 | 81.14 | 1815723.494
104.595 | 127.333 | 129.932 | 2907548.945
128.616 | 156.576 | 159.771 | 3575285.661
141.996 | 172.865 | 176.393 | 3947232.499
146.301 | 178.105 | 181.74 | 4066889.495
144.266 | 175.628 | 179.213 | 4010329.113
133.413 | 162.415 | 165.73 | 3708623.465
115.607 | 140.739 | 143.611 | 3213661.07
87.852 | 106.951 | 109.133 | 2442132.767
53.082 | 64.621 | 65.94 | 1475573.258
16.387 | 19.949 | 20.356 | 455521.385
4.45 | 5.417 | 5.528 | 123697.31
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
24.556 | 29.895 | 30.505 | 682623.235
66.566 | 81.037 | 82.691 | 1850414.959
98.075 | 119.395 | 121.832 | 2726294.941
120.664 | 146.895 | 149.893 | 3354232.219
133.156 | 162.103 | 165.411 | 3701490.897
138.948 | 169.154 | 172.606 | 3862496.11
136.67 | 166.381 | 169.777 | 3799178.089
127.293 | 154.965 | 158.127 | 3538501.716
109.616 | 133.446 | 136.169 | 3047128.055
83.703 | 101.899 | 103.979 | 2326785.854
49.696 | 60.5 | 61.735 | 1381467.065
15.175 | 18.474 | 18.851 | 421838.35
3.798 | 4.624 | 4.718 | 105581.516
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.191 | 18.493 | 18.871 | 422277.922
54.154 | 65.927 | 67.273 | 1505390.165
95.179 | 115.87 | 118.235 | 2645800.53
127.629 | 155.375 | 158.545 | 3547856.05
140.951 | 171.593 | 175.095 | 3918186.114
144.712 | 176.171 | 179.766 | 4022723.066
142.197 | 173.11 | 176.642 | 3952820.561
131.051 | 159.541 | 162.797 | 3642987.064
112.93 | 137.48 | 140.286 | 3139246.928
86.804 | 105.674 | 107.831 | 2412985.605
51.815 | 63.079 | 64.367 | 1440362.218
16.247 | 19.779 | 20.182 | 451634.483
5.126 | 6.241 | 6.368 | 142502.482
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
17.021 | 20.722 | 21.145 | 473165.746
58.509 | 71.229 | 72.682 | 1626450.153
98.968 | 120.482 | 122.941 | 2751115.739
128.043 | 155.878 | 159.06 | 3559355.609
141.08 | 171.75 | 175.255 | 3921770.465
147.294 | 179.314 | 182.974 | 4094496.644
144.287 | 175.654 | 179.238 | 4010913.331
133.581 | 162.621 | 165.94 | 3713317.023
113.181 | 137.786 | 140.598 | 3146230.357
86.095 | 104.812 | 106.951 | 2393293.554
52.244 | 63.601 | 64.899 | 1452280.465
16.767 | 20.412 | 20.829 | 466093.548
4.879 | 5.94 | 6.061 | 135631.948
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.698 | 19.111 | 19.501 | 436381.801
55.833 | 67.97 | 69.357 | 1552043.746
95.585 | 116.364 | 118.739 | 2657081.924
127.458 | 155.166 | 158.333 | 3543094.497
143.602 | 174.819 | 178.387 | 3991858.243
147.59 | 179.675 | 183.342 | 4102734.036
145.641 | 177.301 | 180.92 | 4048535.903
133.349 | 162.338 | 165.651 | 3706857.552
115.269 | 140.328 | 143.192 | 3204274.875
89.747 | 109.257 | 111.487 | 2494798.622
52.977 | 64.494 | 65.811 | 1472670.66
17.341 | 21.111 | 21.542 | 482052.109
5.183 | 6.31 | 6.439 | 144083.122
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.772 | 19.201 | 19.593 | 438438.147
56.887 | 69.254 | 70.667 | 1581356.438
96.975 | 118.056 | 120.466 | 2695720.551
123.925 | 150.865 | 153.944 | 3444883.347
138.573 | 168.697 | 172.14 | 3852065.351
143.505 | 174.702 | 178.267 | 3989177.052
141.114 | 171.791 | 175.297 | 3922709.869
131.433 | 160.006 | 163.271 | 3653603.096
112.849 | 137.382 | 140.185 | 3137000.926
85.701 | 104.332 | 106.461 | 2382334.454
51.569 | 62.779 | 64.061 | 1433515.81
15.757 | 19.183 | 19.574 | 438022.701
4.588 | 5.586 | 5.7 | 127547.968
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
16.634 | 20.25 | 20.664 | 462396.302
57.671 | 70.208 | 71.641 | 1603145.352
98.126 | 119.458 | 121.896 | 2727726.442
124.488 | 151.551 | 154.644 | 3460543.74
139.323 | 169.611 | 173.073 | 3872931.252
146.166 | 177.941 | 181.573 | 4063143.997
143.064 | 174.165 | 177.719 | 3976915.737
133.932 | 163.048 | 166.375 | 3723066.029
116.966 | 142.393 | 145.299 | 3251432.671
87.502 | 106.524 | 108.698 | 2432391.496
52.707 | 64.165 | 65.474 | 1465154.507
16.086 | 19.583 | 19.983 | 447163.363
5.244 | 6.384 | 6.514 | 145772.274
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
18.308 | 22.289 | 22.743 | 508941.261
61.923 | 75.385 | 76.923 | 1721350.994
102.183 | 124.396 | 126.935 | 2840488.778
126.37 | 153.842 | 156.982 | 3512858.792
139.733 | 170.11 | 173.581 | 3884321.158
144.745 | 176.212 | 179.808 | 4023654.735
142.216 | 173.132 | 176.666 | 3953336.894
132.22 | 160.963 | 164.248 | 3675464.388
113.333 | 137.97 | 140.786 | 3150439.553
87.221 | 106.182 | 108.349 | 2424581.558
53.283 | 64.866 | 66.19 | 1481165.703
16.121 | 19.626 | 20.026 | 448138.901
4.557 | 5.547 | 5.66 | 126664.551
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
17.504 | 21.309 | 21.744 | 486575.864
60.011 | 73.057 | 74.548 | 1668197.425
100.39 | 122.214 | 124.708 | 2790657.526
123.608 | 150.48 | 153.551 | 3436085.753
137.231 | 167.063 | 170.473 | 3814757.448
143.848 | 175.119 | 178.693 | 3998704.651
141.344 | 172.071 | 175.583 | 3929104.697
130.575 | 158.961 | 162.205 | 3629745.828
112.821 | 137.348 | 140.151 | 3136227.052
87.569 | 106.605 | 108.781 | 2434246.178
52.981 | 64.498 | 65.815 | 1472767.164
15.715 | 19.131 | 19.522 | 436845.499
3.924 | 4.777 | 4.874 | 109077.098
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.745 | 19.168 | 19.559 | 437684.016
56.466 | 68.741 | 70.144 | 1569647.59
96.922 | 117.992 | 120.4 | 2694252.806
125.149 | 152.355 | 155.464 | 3478905.067
139.008 | 169.227 | 172.681 | 3864165.519
144.036 | 175.349 | 178.927 | 4003946.293
140.359 | 170.872 | 174.359 | 3901723.338
129.037 | 157.089 | 160.294 | 3586994.509
114.17 | 138.99 | 141.827 | 3173724.611
89.124 | 108.499 | 110.713 | 2477485.211
51.739 | 62.986 | 64.272 | 1438241.229
16.796 | 20.448 | 20.865 | 466907.939
4.723 | 5.75 | 5.868 | 131297.849
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.677 | 15.433 | 15.748 | 352399.543
51.28 | 62.427 | 63.701 | 1425475.699
93.211 | 113.475 | 115.791 | 2591106.838
126.227 | 153.667 | 156.803 | 3508866.73
148.819 | 181.171 | 184.869 | 4136897.16
153.856 | 187.303 | 191.126 | 4276915.842
151.154 | 184.013 | 187.768 | 4201791.438
140.253 | 170.743 | 174.227 | 3898775.84
121.785 | 148.26 | 151.286 | 3385399.593
94.239 | 114.725 | 117.067 | 2619661.126
56.165 | 68.375 | 69.77 | 1561285.185
20.976 | 25.537 | 26.058 | 583109.87
6.447 | 7.849 | 8.009 | 179221.784
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.236 | 17.33 | 17.684 | 395723.072
54.004 | 65.744 | 67.085 | 1501208.447
93.954 | 114.379 | 116.713 | 2611750.301
123.533 | 150.388 | 153.457 | 3433988.89
137.679 | 167.609 | 171.029 | 3827216.044
142.709 | 173.733 | 177.279 | 3967053.836
140.376 | 170.892 | 174.38 | 3902187.036
131.733 | 160.37 | 163.643 | 3661924.984
115.041 | 140.05 | 142.908 | 3197928.299
89.598 | 109.076 | 111.302 | 2490661.804
52.717 | 64.177 | 65.486 | 1465428.549
19.132 | 23.291 | 23.766 | 531830.726
5.594 | 6.81 | 6.949 | 155501.537
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.552 | 17.716 | 18.077 | 404524.939
57.617 | 70.142 | 71.574 | 1601641.473
100.201 | 121.984 | 124.473 | 2785403.766
128.133 | 155.987 | 159.171 | 3561847.144
142.594 | 173.593 | 177.136 | 3963856.422
147.265 | 179.279 | 182.938 | 4093694.261
145.135 | 176.687 | 180.292 | 4034496.557
134.879 | 164.2 | 167.551 | 3749378.698
116.839 | 142.239 | 145.142 | 3247912.963
90.34 | 109.979 | 112.223 | 2511281.141
55.032 | 66.996 | 68.363 | 1529795.517
17.644 | 21.479 | 21.918 | 490462.766
4.607 | 5.609 | 5.723 | 128071.926
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.992 | 15.816 | 16.139 | 361148.885
52.457 | 63.861 | 65.164 | 1458211.595
94.313 | 114.816 | 117.159 | 2621729.48
127.197 | 154.849 | 158.009 | 3535849.034
144.998 | 176.52 | 180.122 | 4030686.416
150.211 | 182.866 | 186.598 | 4175596.047
148.488 | 180.769 | 184.458 | 4127708.246
138.172 | 168.209 | 171.642 | 3840920.978
119.894 | 145.958 | 148.937 | 3332834.625
91.786 | 111.74 | 114.02 | 2551488.29
53.963 | 65.694 | 67.035 | 1500071.762
19.376 | 23.588 | 24.07 | 538616.874
5.977 | 7.276 | 7.425 | 166146.078
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.122 | 15.975 | 16.301 | 364773.753
53.803 | 65.499 | 66.836 | 1495620.385
94.702 | 115.289 | 117.642 | 2632535.168
126.273 | 153.724 | 156.861 | 3510161.21
142.025 | 172.9 | 176.429 | 3948034.882
147.591 | 179.676 | 183.342 | 4102753.779
146.635 | 178.512 | 182.155 | 4076179.186
136.102 | 165.69 | 169.071 | 3783392.683
117.638 | 143.212 | 146.135 | 3270129.331
90.447 | 110.11 | 112.357 | 2514269.156
55.385 | 67.425 | 68.801 | 1539597.158
18.484 | 22.503 | 22.962 | 513832.21
4.889 | 5.952 | 6.074 | 135910.373
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.499 | 15.217 | 15.527 | 347460.342
51.131 | 62.246 | 63.516 | 1421338.881
93.93 | 114.35 | 116.684 | 2611089.322
125.363 | 152.616 | 155.73 | 3484860.323
142.103 | 172.995 | 176.526 | 3950204.123
147.825 | 179.961 | 183.633 | 4109261.502
145.772 | 177.461 | 181.083 | 4052184.897
135.028 | 164.382 | 167.736 | 3753527.524
117.586 | 143.149 | 146.07 | 3268685.712
91.509 | 111.402 | 113.675 | 2543774.856
53.934 | 65.659 | 66.999 | 1499269.379
18.98 | 23.107 | 23.578 | 527621.53
5.526 | 6.727 | 6.865 | 153610.721
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.253 | 14.917 | 15.221 | 340613.934
50.863 | 61.92 | 63.183 | 1413891.754
93.076 | 113.31 | 115.622 | 2587340.566
123.72 | 150.616 | 153.69 | 3439194.398
137.663 | 167.59 | 171.011 | 3826785.238
142.273 | 173.202 | 176.736 | 3954925.159
139.775 | 170.16 | 173.633 | 3885474.344
130.218 | 158.526 | 161.762 | 3619819.284
114.758 | 139.705 | 142.556 | 3190053.718
90.559 | 110.246 | 112.496 | 2517377.801
54.605 | 66.475 | 67.832 | 1517909.131
18.875 | 22.979 | 23.448 | 524702.541
5.315 | 6.47 | 6.602 | 147739.851
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.316 | 14.993 | 15.299 | 342355.721
51.922 | 63.21 | 64.5 | 1443345.85
93.368 | 113.665 | 115.985 | 2595453.055
122.172 | 148.731 | 151.766 | 3396152.646
136.692 | 166.407 | 169.804 | 3799778.808
141.882 | 172.726 | 176.251 | 3944059.211
140.614 | 171.182 | 174.676 | 3908807.654
131.628 | 160.243 | 163.513 | 3659018.003
113.908 | 138.67 | 141.5 | 3166422.24
87.403 | 106.403 | 108.575 | 2429633.654
53.027 | 64.555 | 65.872 | 1474057.261
17.853 | 21.735 | 22.178 | 496293.009
4.535 | 5.52 | 5.633 | 126051.824
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.025 | 14.639 | 14.938 | 334271.741
50.303 | 61.239 | 62.489 | 1398340.904
91.861 | 111.831 | 114.113 | 2553568.762
124.767 | 151.89 | 154.99 | 3468289.035
140.541 | 171.093 | 174.585 | 3906775.434
145.506 | 177.138 | 180.753 | 4044802.413
142.996 | 174.082 | 177.635 | 3975024.921
134.469 | 163.702 | 167.043 | 3738000.8
119.234 | 145.154 | 148.116 | 3314476.65
93.353 | 113.648 | 115.967 | 2595054
56.305 | 68.546 | 69.945 | 1565188.478
21.103 | 25.691 | 26.215 | 586629.578
6.278 | 7.643 | 7.799 | 174520.491
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.384 | 12.641 | 12.899 | 288649.685
45.336 | 55.191 | 56.317 | 1260244.899
86.65 | 105.487 | 107.639 | 2408707.383
120.084 | 146.189 | 149.172 | 3338108.128
141.975 | 172.839 | 176.366 | 3946639.515
152.335 | 185.452 | 189.236 | 4234640.229
151.055 | 183.893 | 187.646 | 4199049.987
141.509 | 172.271 | 175.787 | 3933676.704
121.718 | 148.178 | 151.202 | 3383528.52
91.785 | 111.738 | 114.019 | 2551452.156
55.115 | 67.097 | 68.466 | 1532101.779
21.165 | 25.766 | 26.291 | 588342.856
6.606 | 8.042 | 8.207 | 183637.027
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.633 | 12.944 | 13.208 | 295568.471
47.068 | 57.3 | 58.47 | 1308403.39
91.465 | 111.349 | 113.621 | 2542561.41
124.025 | 150.987 | 154.068 | 3447665.315
146.018 | 177.761 | 181.388 | 4059026.922
147.865 | 180.01 | 183.684 | 4110382.827
144.862 | 176.354 | 179.953 | 4026900.401
136.213 | 165.825 | 169.209 | 3786477.202
118.306 | 144.024 | 146.963 | 3288675.931
92.655 | 112.797 | 115.099 | 2575631.718
55.943 | 68.105 | 69.494 | 1555116.147
19.88 | 24.202 | 24.696 | 552631.984
5.79 | 7.049 | 7.193 | 160956.961
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.908 | 14.497 | 14.793 | 331026.075
46.079 | 56.096 | 57.241 | 1280909.136
86.643 | 105.479 | 107.632 | 2408526.493
119.952 | 146.029 | 149.009 | 3334451.399
141.194 | 171.888 | 175.396 | 3924927.362
149.929 | 182.523 | 186.248 | 4167761.983
148.755 | 181.093 | 184.789 | 4135114.856
139.419 | 169.727 | 173.191 | 3875583.934
121.99 | 148.509 | 151.54 | 3391088.542
92.418 | 112.508 | 114.805 | 2569039.609
55.748 | 67.867 | 69.252 | 1549689.232
20.174 | 24.559 | 25.06 | 560788.342
5.463 | 6.65 | 6.786 | 151852.543
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.307 | 17.418 | 17.773 | 397719.048
56.677 | 68.999 | 70.407 | 1575530.468
98.131 | 119.464 | 121.902 | 2727863.463
121.268 | 147.63 | 150.643 | 3371017.289
134.357 | 163.565 | 166.903 | 3734875.764
139.192 | 169.451 | 172.909 | 3869277.875
136.405 | 166.058 | 169.447 | 3791803.34
127.219 | 154.875 | 158.036 | 3536449.753
110.71 | 134.777 | 137.528 | 3077529.29
86.035 | 104.739 | 106.876 | 2391624.145
53.208 | 64.775 | 66.097 | 1479085.231
17.621 | 21.451 | 21.889 | 489821.53
4.868 | 5.926 | 6.047 | 135317.389
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.23 | 13.671 | 13.95 | 312168.268
47.086 | 57.323 | 58.492 | 1308915.23
85.365 | 103.923 | 106.044 | 2372996.511
118.924 | 144.777 | 147.732 | 3305868.712
138.162 | 168.197 | 171.63 | 3840646.936
146.84 | 178.761 | 182.41 | 4081872.518
145.574 | 177.22 | 180.837 | 4046681.221
135.451 | 164.897 | 168.262 | 3765289.007
119.524 | 145.507 | 148.477 | 3322540.887
90.381 | 110.029 | 112.274 | 2512422.209
54.207 | 65.991 | 67.338 | 1506853.527
23.077 | 28.093 | 28.667 | 641488.8
6.875 | 8.37 | 8.54 | 191115.905
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.296 | 12.534 | 12.79 | 286206.402
45.605 | 55.519 | 56.652 | 1267732.543
89.002 | 108.35 | 110.561 | 2474086.133
124.356 | 151.39 | 154.48 | 3456870.62
144.593 | 176.026 | 179.618 | 4019412.757
152.366 | 185.489 | 189.275 | 4235495.247
149.565 | 182.079 | 185.795 | 4157629.392
140.091 | 170.545 | 174.026 | 3894264.203
120.297 | 146.449 | 149.437 | 3344039.258
92.433 | 112.527 | 114.824 | 2569467.063
56.032 | 68.212 | 69.605 | 1557575.931
18.684 | 22.746 | 23.21 | 519384.138
5.181 | 6.307 | 6.436 | 144018.479
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.049 | 14.668 | 14.968 | 334937.103
51.9 | 63.182 | 64.472 | 1442716.732
95.956 | 116.816 | 119.2 | 2667399.788
129.782 | 157.996 | 161.22 | 3607706.998
145.617 | 177.272 | 180.89 | 4047870.541
150.938 | 183.751 | 187.501 | 4195804.321
148.831 | 181.186 | 184.883 | 4137231.462
139.203 | 169.465 | 172.923 | 3869592.434
121.472 | 147.879 | 150.897 | 3376698.503
94.843 | 115.461 | 117.818 | 2636462.587
57.342 | 69.808 | 71.232 | 1594004.69
20.329 | 24.748 | 25.253 | 565102.698
6.162 | 7.502 | 7.655 | 171298.951
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.163 | 13.59 | 13.867 | 310313.586
48.779 | 59.383 | 60.595 | 1355964.514
90.592 | 110.285 | 112.536 | 2518276.688
125.987 | 153.376 | 156.506 | 3502214.251
143.79 | 175.049 | 178.621 | 3997099.885
149.646 | 182.177 | 185.895 | 4159871.011
146.385 | 178.207 | 181.844 | 4069219.883
135.641 | 165.128 | 168.498 | 3770566.893
118.483 | 144.24 | 147.184 | 3293607.397
92.611 | 112.744 | 115.045 | 2574418.272
56.224 | 68.447 | 69.844 | 1562930.468
19.105 | 23.259 | 23.733 | 531092.986
5.102 | 6.211 | 6.337 | 141820.729
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.637 | 14.167 | 14.456 | 323490.179
50.461 | 61.431 | 62.684 | 1402723.255
93.213 | 113.477 | 115.793 | 2591155.09
126.402 | 153.88 | 157.021 | 3513733.553
139.723 | 170.097 | 173.568 | 3884030.725
144.34 | 175.719 | 179.305 | 4012397.467
141.6 | 172.382 | 175.9 | 3936208.756
130.792 | 159.225 | 162.474 | 3635773.462
115.094 | 140.114 | 142.973 | 3199391.661
88.707 | 107.991 | 110.195 | 2465889.258
54.735 | 66.634 | 67.994 | 1521533.999
17.082 | 20.795 | 21.22 | 474842.89
4.546 | 5.534 | 5.647 | 126366.383
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.516 | 15.236 | 15.547 | 347907.649
51.799 | 63.059 | 64.346 | 1439906.255
94.098 | 114.554 | 116.892 | 2615750.098
119.132 | 145.03 | 147.99 | 3311646.43
133.196 | 162.152 | 165.461 | 3702607.839
139.898 | 170.311 | 173.786 | 3888909.556
136.562 | 166.25 | 169.643 | 3796182.339
127.815 | 155.601 | 158.777 | 3553025.424
110.03 | 133.949 | 136.683 | 3058623.231
84.86 | 103.308 | 105.416 | 2358952.892
53.124 | 64.672 | 65.992 | 1476738.452
15.656 | 19.059 | 19.448 | 435200.216
3.766 | 4.585 | 4.678 | 104690.364
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.218 | 14.874 | 15.178 | 339638.396
51.687 | 62.923 | 64.207 | 1436797.61
92.536 | 112.653 | 114.952 | 2572337.8
122.029 | 148.557 | 151.589 | 3392181.358
134.921 | 164.252 | 167.604 | 3750560.283
141.365 | 172.096 | 175.608 | 3929676.907
139.796 | 170.186 | 173.66 | 3886067.328
127.446 | 155.152 | 158.318 | 3542767.82
107.448 | 130.807 | 133.476 | 2986866.044
84.876 | 103.328 | 105.436 | 2359404.472
53.002 | 64.524 | 65.841 | 1473355.765
16.159 | 19.672 | 20.073 | 449191.2
4.453 | 5.421 | 5.531 | 123781.696
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.586 | 15.323 | 15.635 | 349879.499
53.54 | 65.179 | 66.509 | 1488310.279
93.06 | 113.291 | 115.603 | 2586905.377
122.704 | 149.379 | 152.427 | 3410946.013
135.609 | 165.089 | 168.458 | 3769675.741
139.653 | 170.012 | 173.482 | 3882091.657
136.599 | 166.294 | 169.688 | 3797194.121
123.213 | 149.998 | 153.059 | 3425086.136
106.237 | 129.332 | 131.972 | 2953195.127
85.551 | 104.149 | 106.274 | 2378157.119
54.191 | 65.972 | 67.319 | 1506418.338
16.677 | 20.303 | 20.717 | 463597.63
4.374 | 5.325 | 5.434 | 121592.712
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.918 | 14.509 | 14.805 | 331300.117
52.019 | 63.327 | 64.619 | 1446022.658
92.661 | 112.805 | 115.107 | 2575809.256
121.356 | 147.738 | 150.753 | 3373476.963
136.071 | 165.651 | 169.032 | 3782513.649
141.398 | 172.137 | 175.65 | 3930608.576
138.456 | 168.555 | 171.995 | 3848819.685
128.468 | 156.396 | 159.587 | 3571172.969
111.938 | 136.272 | 139.053 | 3111663.905
86.993 | 105.904 | 108.065 | 2418234.982
53.871 | 65.582 | 66.921 | 1497515.584
16.505 | 20.093 | 20.503 | 458807.568
4.342 | 5.286 | 5.394 | 120701.56
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.996 | 18.256 | 18.628 | 416858.632
57.662 | 70.197 | 71.629 | 1602891.053
94.791 | 115.398 | 117.753 | 2635018.968
118.1 | 143.774 | 146.708 | 3282962.856
131.714 | 160.347 | 163.619 | 3661396.643
138.42 | 168.511 | 171.95 | 3847815.638
136.814 | 166.556 | 169.955 | 3803173.503
126.672 | 154.21 | 157.357 | 3521257.331
106.618 | 129.796 | 132.445 | 2963787.033
82.792 | 100.79 | 102.847 | 2301460.841
50.104 | 60.996 | 62.241 | 1392796.711
15.424 | 18.777 | 19.161 | 428761.519
3.389 | 4.126 | 4.211 | 94215.736
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.278 | 17.382 | 17.737 | 396904.657
58.746 | 71.517 | 72.977 | 1633034.637
96.765 | 117.801 | 120.205 | 2689890.198
121.003 | 147.308 | 150.314 | 3363658.931
135.644 | 165.132 | 168.502 | 3770655.662
143.03 | 174.123 | 177.677 | 3975964.325
139.977 | 170.407 | 173.885 | 3891107.306
131.381 | 159.942 | 163.206 | 3652147.469
113.928 | 138.695 | 141.525 | 3166986.715
88.32 | 107.521 | 109.715 | 2455148.213
54.418 | 66.248 | 67.6 | 1512720.014
16.909 | 20.585 | 21.005 | 470040.71
4.259 | 5.185 | 5.291 | 118395.298
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.513 | 11.581 | 11.817 | 264441.614
47.45 | 57.765 | 58.944 | 1319019.422
89.931 | 109.481 | 111.715 | 2499910.978
123.243 | 150.035 | 153.097 | 3425929.036
142.206 | 173.121 | 176.654 | 3953074.86
146.028 | 177.773 | 181.402 | 4059309.73
140.351 | 170.862 | 174.349 | 3901497.548
132.702 | 161.55 | 164.847 | 3688866.771
115.701 | 140.853 | 143.728 | 3216269.883
91.689 | 111.621 | 113.899 | 2548778.7
54.454 | 66.292 | 67.645 | 1513724.061
17.338 | 21.107 | 21.538 | 481963.34
4.666 | 5.68 | 5.796 | 129700.818
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
7.906 | 9.624 | 9.821 | 219763.345
41.864 | 50.965 | 52.005 | 1163743.675
82.811 | 100.813 | 102.871 | 2301989.182
117.701 | 143.289 | 146.213 | 3271883.126
139.109 | 169.351 | 172.807 | 3866988.004
148.946 | 181.326 | 185.026 | 4140428.876
148.805 | 181.154 | 184.851 | 4136505.84
140.068 | 170.518 | 173.998 | 3893639.358
121.971 | 148.487 | 151.517 | 3390576.592
91.835 | 111.799 | 114.081 | 2552843.14
55.55 | 67.626 | 69.006 | 1544185.556
20.163 | 24.546 | 25.047 | 560490.174
6.383 | 7.771 | 7.93 | 177443.863
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.967 | 10.916 | 11.139 | 249261.31
46.052 | 56.063 | 57.207 | 1280155.005
88.355 | 107.563 | 109.758 | 2456111.743
121.738 | 148.202 | 151.227 | 3384080.987
142.42 | 173.381 | 176.92 | 3959018.108
147.717 | 179.829 | 183.499 | 4106253.744
145.047 | 176.579 | 180.182 | 4032036.883
134.117 | 163.273 | 166.605 | 3728206.894
117.826 | 143.441 | 146.368 | 3275354.582
91.823 | 111.785 | 114.066 | 2552516.463
53.75 | 65.435 | 66.77 | 1494152.64
17.541 | 21.355 | 21.79 | 487616.045
4.981 | 6.064 | 6.188 | 138466.551
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.112 | 11.093 | 11.32 | 253301.624
46.561 | 56.684 | 57.84 | 1294323.527
87.662 | 106.719 | 108.897 | 2436842.873
120.897 | 147.179 | 150.183 | 3360715.816
142.152 | 173.055 | 176.587 | 3951570.981
153.097 | 186.379 | 190.182 | 4255812.033
152.526 | 185.684 | 189.474 | 4239946.624
141.325 | 172.047 | 175.559 | 3928564.348
120.623 | 146.845 | 149.842 | 3353091.151
90.799 | 110.538 | 112.794 | 2524046.671
54.27 | 66.068 | 67.416 | 1508607.322
19.16 | 23.325 | 23.801 | 532608.983
5.463 | 6.65 | 6.786 | 151852.543
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.897 | 12.049 | 12.295 | 275126.672
47.368 | 57.666 | 58.842 | 1316749.294
90.345 | 109.986 | 112.23 | 2511434.553
124.302 | 151.324 | 154.412 | 3455362.358
143.565 | 174.775 | 178.342 | 3990846.461
149.902 | 182.49 | 186.214 | 4167007.852
146.536 | 178.392 | 182.033 | 4073437.735
135.652 | 165.141 | 168.512 | 3770869.444
117.999 | 143.651 | 146.583 | 3280156.762
91.064 | 110.86 | 113.123 | 2531405.029
53.265 | 64.844 | 66.167 | 1480661.488
17.214 | 20.956 | 21.383 | 478511.627
4.302 | 5.237 | 5.344 | 119584.618
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.84 | 10.761 | 10.981 | 245725.211
43.905 | 53.45 | 54.541 | 1220485.978
86.333 | 105.101 | 107.246 | 2399897.781
118.436 | 144.184 | 147.126 | 3292317.19
140.566 | 171.123 | 174.616 | 3907464.922
150.696 | 183.456 | 187.2 | 4189070.808
148.423 | 180.689 | 184.376 | 4125885.425
140.712 | 171.301 | 174.797 | 3911524.979
109.03 | 132.733 | 135.441 | 3030842.817
88.798 | 108.102 | 110.309 | 2468425.693
55.614 | 67.704 | 69.085 | 1545963.477
19.378 | 23.591 | 24.072 | 538677.134
5.843 | 7.114 | 7.259 | 162436.714
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
6.682 | 8.135 | 8.301 | 185753.633
38.974 | 47.447 | 48.415 | 1083410.411
79.963 | 97.346 | 99.333 | 2222821.112
112.34 | 136.762 | 139.553 | 3122848.795
135.543 | 165.008 | 168.376 | 3767833.177
146.557 | 178.418 | 182.059 | 4074026.336
147.321 | 179.347 | 183.007 | 4095246.392
140.313 | 170.816 | 174.302 | 3900445.249
120.276 | 146.423 | 149.411 | 3343450.657
91.196 | 111.021 | 113.287 | 2535078.149
54.808 | 66.723 | 68.085 | 1523566.219
18.185 | 22.138 | 22.59 | 505506.049
5.127 | 6.241 | 6.368 | 142510.217
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
16.764 | 20.408 | 20.824 | 466000.396
63.972 | 77.879 | 79.468 | 1778302.696
101.007 | 122.965 | 125.475 | 2807809.79
128.017 | 155.846 | 159.027 | 3558625.604
142.39 | 173.345 | 176.883 | 3958191.599
150.079 | 182.705 | 186.433 | 4171918.544
146.581 | 178.446 | 182.088 | 4074675.307
136.715 | 166.436 | 169.832 | 3800427.669
121.498 | 147.911 | 150.929 | 3377424.125
93.979 | 114.41 | 116.745 | 2612456.18
53.682 | 65.352 | 66.685 | 1492257.441
19.674 | 23.951 | 24.44 | 546902.518
6.832 | 8.317 | 8.487 | 189914.577
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
16.631 | 20.247 | 20.66 | 462319.541
65.19 | 79.362 | 80.982 | 1812167.652
103.779 | 126.34 | 128.919 | 2884873.262
128.963 | 156.998 | 160.203 | 3584930.538
145.397 | 177.005 | 180.617 | 4041766.146
149.163 | 181.589 | 185.295 | 4146444.502
146.141 | 177.911 | 181.542 | 4062454.509
135.435 | 164.878 | 168.243 | 3764853.818
119.097 | 144.988 | 147.947 | 3310682.9
93.624 | 113.977 | 116.303 | 2602573.505
59.907 | 72.931 | 74.419 | 1665314.57
20.654 | 25.143 | 25.657 | 574130.465
7.001 | 8.523 | 8.696 | 194611.487
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
16.462 | 20.041 | 20.45 | 457618.248
65.177 | 79.346 | 80.966 | 1811804.841
106.036 | 129.087 | 131.722 | 2947602.682
133.023 | 161.941 | 165.246 | 3697793.651
148.21 | 180.43 | 184.112 | 4119970.686
154.012 | 187.493 | 191.319 | 4281249.941
149.253 | 181.699 | 185.407 | 4148952.428
137.562 | 167.467 | 170.885 | 3823974.761
118.574 | 144.35 | 147.296 | 3296123.058
93.959 | 114.384 | 116.719 | 2611875.314
59.965 | 73.001 | 74.491 | 1666919.336
22.363 | 27.224 | 27.78 | 621643.337
7.284 | 8.868 | 9.049 | 202490.451
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.888 | 19.341 | 19.736 | 441643.296
66.424 | 80.865 | 82.515 | 1846479.805
106.446 | 129.586 | 132.231 | 2958996.971
134.404 | 163.623 | 166.962 | 3736194.37
150.097 | 182.727 | 186.456 | 4172422.759
155.737 | 189.593 | 193.463 | 4329206.768
153.6 | 186.992 | 190.808 | 4269807.4
143.275 | 174.422 | 177.981 | 3982782.224
123.542 | 150.399 | 153.468 | 3434238.806
96.426 | 117.388 | 119.784 | 2680463.486
59.951 | 72.984 | 74.473 | 1666528.016
21.565 | 26.254 | 26.789 | 599479.494
7.074 | 8.612 | 8.787 | 196643.707
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.915 | 19.374 | 19.77 | 442397.427
64.861 | 78.961 | 80.572 | 1803010.599
108.07 | 131.563 | 134.248 | 3004138.938
137.597 | 167.509 | 170.928 | 3824938.291
152.702 | 185.898 | 189.692 | 4244833.19
158.99 | 193.553 | 197.504 | 4419632.106
156.404 | 190.404 | 194.29 | 4347729.242
146.128 | 177.895 | 181.526 | 4062091.698
127.317 | 154.994 | 158.158 | 3539171.461
98.993 | 120.513 | 122.973 | 2751821.618
61.834 | 75.277 | 76.813 | 1718883.585
20.734 | 25.242 | 25.757 | 576376.357
6.457 | 7.861 | 8.021 | 179495.826
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.484 | 18.85 | 19.235 | 430426.545
62.486 | 76.07 | 77.622 | 1736994.996
105.291 | 128.18 | 130.796 | 2926890.193
133.327 | 162.311 | 165.624 | 3706244.825
149.297 | 181.753 | 185.462 | 4150182.265
155.907 | 189.8 | 193.674 | 4333932.187
153.528 | 186.904 | 190.718 | 4267799.306
143.067 | 174.168 | 177.723 | 3976992.498
123.456 | 150.294 | 153.361 | 3431843.775
95.515 | 116.279 | 118.652 | 2655138.473
59.271 | 72.156 | 73.628 | 1647621.957
20.033 | 24.388 | 24.886 | 556881.697
6.391 | 7.78 | 7.939 | 177653.262
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
15.17 | 18.468 | 18.845 | 421701.329
64.994 | 79.123 | 80.737 | 1806707.845
104.882 | 127.682 | 130.288 | 2915520.03
132.087 | 160.801 | 164.083 | 3671767.142
148.13 | 180.332 | 184.013 | 4117741.185
155.418 | 189.205 | 193.066 | 4320340.148
152.924 | 186.168 | 189.968 | 4251002.228
142.117 | 173.012 | 176.543 | 3950591.06
122.437 | 149.054 | 152.096 | 3403527.395
94.95 | 115.592 | 117.951 | 2639446.219
58.918 | 71.727 | 73.19 | 1637820.316
19.913 | 24.242 | 24.737 | 553547.262
6.186 | 7.531 | 7.684 | 171959.93
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.819 | 18.04 | 18.408 | 411931.549
65.582 | 79.839 | 81.468 | 1823057.726
105.904 | 128.927 | 131.558 | 2943941.57
132.526 | 161.336 | 164.628 | 3683975.822
149.292 | 181.747 | 185.457 | 4150049.627
154.29 | 187.831 | 191.664 | 4288971.11
153.483 | 186.849 | 190.663 | 4266549.726
142.105 | 172.997 | 176.527 | 3950247.992
121.912 | 148.415 | 151.444 | 3388935.692
94.014 | 114.452 | 116.788 | 2613419.71
58.028 | 70.643 | 72.085 | 1613076.279
19.038 | 23.177 | 23.65 | 529226.296
5.682 | 6.917 | 7.058 | 157944.82
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.533 | 17.692 | 18.054 | 403988.973
65.139 | 79.3 | 80.918 | 1810748.159
104.001 | 126.61 | 129.194 | 2891037.917
130.182 | 158.482 | 161.717 | 3618815.237
145.471 | 177.095 | 180.71 | 4043826.875
152.4 | 185.531 | 189.317 | 4236446.659
149.795 | 182.36 | 186.081 | 4164036.228
139.93 | 170.349 | 173.826 | 3889788.7
120.455 | 146.641 | 149.633 | 3348425.992
92.898 | 113.093 | 115.401 | 2582389.357
57.093 | 69.504 | 70.923 | 1587073.896
18.025 | 21.944 | 22.391 | 501066.68
5.358 | 6.523 | 6.656 | 148945.562
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.951 | 16.984 | 17.33 | 387812.247
64.397 | 78.396 | 79.996 | 1790112.431
103.37 | 125.841 | 128.41 | 2873486.708
129.386 | 157.513 | 160.728 | 3596687.638
145.373 | 176.975 | 180.587 | 4041088.776
151.47 | 184.398 | 188.162 | 4210585.68
149.069 | 181.475 | 185.179 | 4143840.072
139.457 | 169.774 | 173.239 | 3876652.624
120.745 | 146.994 | 149.994 | 3356490.229
92.769 | 112.936 | 115.241 | 2578805.006
57.144 | 69.566 | 70.986 | 1588489.006
17.691 | 21.537 | 21.976 | 491776.989
5.315 | 6.47 | 6.602 | 147739.851
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.139 | 17.212 | 17.564 | 393029.873
65.137 | 79.298 | 80.916 | 1810699.907
105.018 | 127.848 | 130.457 | 2919306.045
131.243 | 159.774 | 163.034 | 3648308.819
147.586 | 179.67 | 183.337 | 4102621.141
153.635 | 187.034 | 190.851 | 4270770.93
152.259 | 185.359 | 189.142 | 4232523.623
142.805 | 173.849 | 177.397 | 3969706.518
122.579 | 149.226 | 152.272 | 3407462.549
93.748 | 114.128 | 116.457 | 2606020.835
54.125 | 65.891 | 67.236 | 1504571.391
17.422 | 21.209 | 21.642 | 484293.728
5.476 | 6.666 | 6.802 | 152215.354
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.544 | 16.488 | 16.824 | 376490.336
57.899 | 70.486 | 71.924 | 1609487.545
101.455 | 123.51 | 126.031 | 2820256.378
131.581 | 160.186 | 163.455 | 3657715.788
151.162 | 184.024 | 187.779 | 4202033.619
157.458 | 191.688 | 195.6 | 4377041.934
153.723 | 187.141 | 190.96 | 4273214.213
138.87 | 169.059 | 172.51 | 3860331.252
127.607 | 155.347 | 158.518 | 3547231.315
97.57 | 118.781 | 121.205 | 2712267.713
56.787 | 69.132 | 70.543 | 1578574.47
18.508 | 22.532 | 22.992 | 514497.572
5.875 | 7.152 | 7.298 | 163311.475
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.474 | 16.403 | 16.738 | 374551.268
58.447 | 71.153 | 72.605 | 1624720.484
102.943 | 125.322 | 127.879 | 2861624.338
132.485 | 161.286 | 164.578 | 3682839.137
148.543 | 180.835 | 184.525 | 4129219.86
160.445 | 195.324 | 199.31 | 4460068.397
161.845 | 197.028 | 201.049 | 4498981.066
149.922 | 182.513 | 186.238 | 4167543.928
129.294 | 157.402 | 160.614 | 3594143.468
95.201 | 115.897 | 118.262 | 2646413.257
55.569 | 67.649 | 69.03 | 1544713.897
18.458 | 22.47 | 22.929 | 513090.197
6.521 | 7.939 | 8.101 | 181278.13
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.249 | 16.129 | 16.458 | 368293.461
54.145 | 65.916 | 67.261 | 1505135.866
93.614 | 113.965 | 116.291 | 2602299.463
122.953 | 149.682 | 152.737 | 3417869.182
141.64 | 172.432 | 175.951 | 3937342.089
147.844 | 179.983 | 183.657 | 4109777.835
147.64 | 179.736 | 183.404 | 4104125.02
144.962 | 176.476 | 180.077 | 4029682.369
121.16 | 147.499 | 150.51 | 3368025.922
91.818 | 111.778 | 114.06 | 2552367.434
53.981 | 65.716 | 67.058 | 1500575.977
17.933 | 21.832 | 22.277 | 498510.502
6.653 | 8.1 | 8.265 | 184951.25
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.512 | 11.58 | 11.817 | 264421.871
55.37 | 67.407 | 68.782 | 1539181.712
98.242 | 119.599 | 122.04 | 2730947.982
129.924 | 158.169 | 161.397 | 3611658.543
150.319 | 182.997 | 186.732 | 4178591.797
157.906 | 192.234 | 196.157 | 4389504.913
155.855 | 189.737 | 193.609 | 4332488.568
142.973 | 174.055 | 177.607 | 3974400.076
124.743 | 151.861 | 154.96 | 3467623.673
94.393 | 114.913 | 117.258 | 2623946.973
55.159 | 67.15 | 68.521 | 1533319.608
19.324 | 23.524 | 24.004 | 537156.864
6.512 | 7.928 | 8.089 | 181023.831
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
12.399 | 15.095 | 15.403 | 344678.374
51.49 | 62.683 | 63.962 | 1431318.06
93.873 | 114.28 | 116.612 | 2609492.291
127.064 | 154.686 | 157.843 | 3532135.397
148.918 | 181.292 | 184.992 | 4139655.002
160.363 | 195.224 | 199.208 | 4457786.261
160.257 | 195.096 | 199.077 | 4454855.154
147.373 | 179.41 | 183.072 | 4096690.011
125.872 | 153.236 | 156.363 | 3499016.837
94.522 | 115.071 | 117.419 | 2627547.715
56.231 | 68.455 | 69.852 | 1563115.741
19.549 | 23.798 | 24.284 | 543414.671
6.511 | 7.926 | 8.088 | 180987.697
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.881 | 10.812 | 11.033 | 246882.67
35.201 | 42.853 | 43.727 | 978514
83.709 | 101.906 | 103.986 | 2326947.001
133.839 | 162.935 | 166.26 | 3720485.725
154.761 | 188.405 | 192.25 | 4302075.325
165.773 | 201.811 | 205.93 | 4608191.833
162.522 | 197.853 | 201.891 | 4517814.747
150.225 | 182.882 | 186.614 | 4175966.593
128.392 | 156.303 | 159.493 | 3569056.363
95.341 | 116.067 | 118.436 | 2650300.159
55.113 | 67.094 | 68.464 | 1532041.519
19.249 | 23.434 | 23.912 | 535092.783
6.055 | 7.371 | 7.522 | 168315.319
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.873 | 14.454 | 14.749 | 330046.154
55.75 | 67.87 | 69.255 | 1549753.875
109.375 | 133.153 | 135.87 | 3040435.059
142.232 | 173.152 | 176.685 | 3953784.091
159.851 | 194.601 | 198.573 | 4443561.752
168.094 | 204.636 | 208.812 | 4672699.174
166.496 | 202.691 | 206.827 | 4628282.829
156.004 | 189.918 | 193.794 | 4336625.386
135.932 | 165.483 | 168.86 | 3778667.264
103.386 | 125.861 | 128.429 | 2873933.905
60.189 | 73.274 | 74.769 | 1673148.634
19.33 | 23.532 | 24.012 | 537334.402
5.759 | 7.011 | 7.154 | 160089.935
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.049 | 12.234 | 12.484 | 279352.259
41.192 | 50.147 | 51.17 | 1145063.406
96.314 | 117.251 | 119.644 | 2677338.45
138.13 | 168.159 | 171.59 | 3839767.792
155.345 | 189.116 | 192.976 | 4318312.311
162.929 | 198.348 | 202.396 | 4529120.267
161.114 | 196.138 | 200.141 | 4478659.897
149.728 | 182.278 | 185.998 | 4162169.538
128.72 | 156.703 | 159.901 | 3578184.907
98.298 | 119.667 | 122.109 | 2732500.113
57.422 | 69.905 | 71.331 | 1596222.183
16.538 | 20.134 | 20.544 | 459734.854
4.998 | 6.084 | 6.208 | 138925.866
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.956 | 14.555 | 14.852 | 332352.416
51.637 | 62.863 | 64.146 | 1435423.017
101.911 | 124.065 | 126.597 | 2832928.756
136.028 | 165.599 | 168.979 | 3781324.329
154.096 | 187.595 | 191.423 | 4283580.329
158.907 | 193.452 | 197.4 | 4417321.461
156.332 | 190.317 | 194.201 | 4345737.539
145.327 | 176.92 | 180.531 | 4039827.078
124.364 | 151.4 | 154.49 | 3457096.41
93.105 | 113.346 | 115.659 | 2588159.34
50.954 | 62.031 | 63.297 | 1416428.189
15.017 | 18.281 | 18.655 | 417439.608
4.785 | 5.825 | 5.944 | 133011.127
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
7.146 | 8.7 | 8.877 | 198651.801
43.087 | 52.454 | 53.525 | 1197745.652
82.784 | 100.781 | 102.837 | 2301247.059
138.658 | 168.801 | 172.246 | 3854436.256
154.886 | 188.557 | 192.405 | 4305546.781
160.6 | 195.513 | 199.503 | 4464382.753
156.727 | 190.798 | 194.692 | 4356720.765
145.613 | 177.268 | 180.886 | 4047774.037
124.248 | 151.258 | 154.345 | 3453858.479
94.457 | 114.992 | 117.338 | 2625741.285
54.258 | 66.053 | 67.401 | 1508268.637
15.653 | 19.056 | 19.445 | 435127.838
4.644 | 5.654 | 5.769 | 129100.099
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.154 | 13.578 | 13.855 | 310047.279
40.136 | 48.861 | 49.858 | 1115702.462
95.211 | 115.909 | 118.274 | 2646687.299
130.959 | 159.428 | 162.682 | 3640414.495
150.408 | 183.106 | 186.843 | 4181075.597
151.155 | 184.015 | 187.77 | 4201831.955
155.432 | 189.222 | 193.084 | 4320731.468
146.499 | 178.346 | 181.986 | 4072393.171
127.231 | 154.89 | 158.051 | 3536788.438
97.093 | 118.2 | 120.613 | 2699006.734
55.513 | 67.581 | 68.96 | 1543157.383
16.492 | 20.077 | 20.487 | 458444.757
4.808 | 5.854 | 5.973 | 133664.371
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.745 | 13.081 | 13.348 | 298693.507
56.173 | 68.385 | 69.78 | 1561510.975
103.094 | 125.505 | 128.067 | 2865813.791
135.057 | 164.417 | 167.773 | 3754334.29
156.945 | 191.063 | 194.962 | 4362772.525
161.848 | 197.032 | 201.053 | 4499069.835
158.625 | 193.109 | 197.05 | 4409487.397
144.881 | 176.377 | 179.977 | 4027428.742
125.234 | 152.459 | 155.57 | 3481275.972
96.411 | 117.37 | 119.765 | 2680048.04
53.537 | 65.176 | 66.506 | 1488237.901
16.325 | 19.874 | 20.28 | 453808.107
5.192 | 6.321 | 6.45 | 144333.038
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
2.315 | 2.818 | 2.876 | 64350.577
24.644 | 30.001 | 30.613 | 685050.127
80.679 | 98.218 | 100.223 | 2242731.218
102.017 | 124.194 | 126.729 | 2835876.254
139.119 | 169.362 | 172.818 | 3867245.655
133.907 | 163.017 | 166.344 | 3722364.533
146.5 | 178.348 | 181.988 | 4072433.688
128.396 | 156.308 | 159.498 | 3569169.258
78.722 | 95.835 | 97.791 | 2188319.303
93.64 | 113.996 | 116.323 | 2603013.077
55.036 | 67 | 68.367 | 1529892.021
15.449 | 18.807 | 19.191 | 429446.624
4.644 | 5.654 | 5.769 | 129100.099
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.705 | 13.032 | 13.298 | 297576.565
56.945 | 69.325 | 70.74 | 1582977.595
101.216 | 123.219 | 125.734 | 2813611.634
136.264 | 165.887 | 169.272 | 3787892.312
154.459 | 188.037 | 191.875 | 4293676.786
160.708 | 195.645 | 199.638 | 4467394.894
159.7 | 194.417 | 198.385 | 4439360.291
146.246 | 178.038 | 181.672 | 4065361.49
126.731 | 154.281 | 157.43 | 3522886.223
95.944 | 116.802 | 119.185 | 2667073.111
54.133 | 65.901 | 67.246 | 1504797.181
16.266 | 19.802 | 20.206 | 452162.824
4.484 | 5.459 | 5.571 | 124653.105
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.727 | 13.059 | 13.325 | 298189.292
59.821 | 72.826 | 74.312 | 1662919.539
107.95 | 131.417 | 134.099 | 3000804.503
140.412 | 170.937 | 174.425 | 3903203.091
156.725 | 190.796 | 194.689 | 4356668.13
162.532 | 197.865 | 201.903 | 4518088.789
157.342 | 191.547 | 195.456 | 4373820.394
146.087 | 177.845 | 181.474 | 4060946.247
126.265 | 153.714 | 156.851 | 3509935.42
93.522 | 113.853 | 116.177 | 2599743.285
53.666 | 65.333 | 66.666 | 1491822.252
15.421 | 18.774 | 19.157 | 428684.758
4.068 | 4.953 | 5.054 | 113093.286
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.014 | 12.191 | 12.44 | 278372.338
49.294 | 60.01 | 61.234 | 1370277.792
103.011 | 125.404 | 127.963 | 2863503.146
138.705 | 168.858 | 172.304 | 3855738.471
155.983 | 189.893 | 193.768 | 4336048.793
161.442 | 196.538 | 200.549 | 4487788.441
159.153 | 193.752 | 197.706 | 4424167.869
147.655 | 179.754 | 183.422 | 4104536.083
127.44 | 155.145 | 158.311 | 3542606.673
96.504 | 117.483 | 119.88 | 2682628.344
53.727 | 65.406 | 66.741 | 1493499.396
15.41 | 18.76 | 19.142 | 428365.816
4.074 | 4.959 | 5.06 | 113238.042
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.889 | 12.039 | 12.284 | 274896.499
59.757 | 72.748 | 74.232 | 1661137.235
105 | 127.826 | 130.435 | 2918806.213
137.002 | 166.785 | 170.189 | 3808403.137
153.435 | 186.79 | 190.602 | 4265202.611
159.205 | 193.815 | 197.77 | 4425607.105
155.755 | 189.615 | 193.485 | 4329706.6
145.252 | 176.829 | 180.438 | 4037746.606
125.461 | 152.735 | 155.852 | 3487582.031
95.101 | 115.775 | 118.138 | 2643631.289
54.288 | 66.09 | 67.439 | 1509111.537
15.206 | 18.512 | 18.89 | 422705.376
3.522 | 4.287 | 4.375 | 97896.591
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.316 | 11.341 | 11.572 | 258962.064
62.918 | 76.596 | 78.159 | 1749006.395
108.19 | 131.709 | 134.397 | 3007473.373
136.404 | 166.057 | 169.445 | 3791774.831
153.195 | 186.498 | 190.304 | 4258533.741
159.878 | 194.634 | 198.606 | 4444311.5
156.317 | 190.298 | 194.182 | 4345310.085
143.885 | 175.164 | 178.739 | 3999732.824
122.999 | 149.738 | 152.794 | 3419147.271
90.075 | 109.656 | 111.894 | 2503910.775
50.363 | 61.311 | 62.562 | 1399989.539
13.44 | 16.362 | 16.695 | 373607.481
2.792 | 3.399 | 3.468 | 77611.556
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.446 | 11.5 | 11.735 | 262591.315
61.277 | 74.598 | 76.121 | 1703388.722
106.055 | 129.11 | 131.745 | 2948126.64
134.382 | 163.595 | 166.934 | 3735565.252
149.518 | 182.021 | 185.736 | 4156310.786
154.926 | 188.606 | 192.455 | 4306663.723
150.995 | 183.82 | 187.572 | 4197384.961
138.763 | 168.928 | 172.376 | 3857343.237
118.628 | 144.417 | 147.364 | 3297643.328
88.985 | 108.33 | 110.541 | 2473626.818
49.168 | 59.857 | 61.079 | 1366786.593
12.71 | 15.473 | 15.789 | 353314.821
2.401 | 2.923 | 2.982 | 66741.225
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.916 | 10.854 | 11.076 | 247846.2
52.486 | 63.896 | 65.2 | 1459013.978
105.643 | 128.609 | 131.233 | 2936679.716
138.095 | 168.115 | 171.546 | 3838775.863
155.364 | 189.139 | 192.999 | 4318836.269
161.337 | 196.41 | 200.418 | 4484865.069
156.615 | 190.662 | 194.553 | 4353612.12
143.099 | 174.208 | 177.763 | 3977895.658
120.503 | 146.7 | 149.694 | 3349773.107
86.745 | 105.603 | 107.758 | 2411356.713
48.279 | 58.774 | 59.974 | 1342062.299
14.055 | 17.11 | 17.459 | 390695.102
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.184 | 11.18 | 11.409 | 255293.327
50.108 | 61.002 | 62.247 | 1392925.997
95.886 | 116.731 | 119.113 | 2665456.337
130.404 | 158.752 | 161.992 | 3624979.892
151.647 | 184.614 | 188.381 | 4215508.38
162.02 | 197.242 | 201.268 | 4503864.28
159.528 | 194.207 | 198.171 | 4434570.229
145.315 | 176.905 | 180.515 | 4039484.01
123.764 | 150.67 | 153.745 | 3440424.235
92.636 | 112.774 | 115.076 | 2575107.76
54.017 | 65.759 | 67.101 | 1501559.25
17.138 | 20.863 | 21.289 | 476395.021
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
2.124 | 2.585 | 2.638 | 59032.174
25.218 | 30.7 | 31.327 | 701013.071
80.348 | 97.815 | 99.811 | 2233525.913
114.675 | 139.605 | 142.454 | 3187763.847
132.908 | 161.801 | 165.103 | 3694596.237
162.43 | 197.741 | 201.777 | 4515258.569
160.821 | 195.782 | 199.777 | 4470523.282
149.603 | 182.125 | 185.842 | 4158681.691
117.898 | 143.528 | 146.457 | 3277346.285
92.553 | 112.673 | 114.973 | 2572801.498
52.817 | 64.299 | 65.612 | 1468219.283
14.468 | 17.614 | 17.973 | 402194.551
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.079 | 11.053 | 11.279 | 252386.346
67.532 | 82.213 | 83.891 | 1877267.977
111.151 | 135.315 | 138.076 | 3089802.613
139.888 | 170.298 | 173.774 | 3888623.506
158.314 | 192.73 | 196.663 | 4400834.559
165.394 | 201.349 | 205.458 | 4597643.796
161.424 | 196.517 | 200.527 | 4487300.617
148.826 | 181.179 | 184.877 | 4137082.433
127.145 | 154.785 | 157.944 | 3534393.407
90.715 | 110.435 | 112.689 | 2521699.892
47.518 | 57.848 | 59.029 | 1320914.621
12.705 | 15.467 | 15.783 | 353177.8
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.398 | 11.441 | 11.675 | 261248.583
67.431 | 82.09 | 83.765 | 1874457.5
111.54 | 135.788 | 138.559 | 3100608.301
138.62 | 168.755 | 172.199 | 3853383.957
158.393 | 192.826 | 196.761 | 4403027.926
164.793 | 200.617 | 204.711 | 4580931.104
158.418 | 192.856 | 196.792 | 4403717.414
145.49 | 177.119 | 180.733 | 4044362.841
123.151 | 149.922 | 152.982 | 3423356.467
91.121 | 110.93 | 113.194 | 2532997.677
46.643 | 56.782 | 57.941 | 1296577.264
10.904 | 13.274 | 13.545 | 303104.367
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.461 | 10.301 | 10.511 | 235209.956
64.318 | 78.3 | 79.898 | 1787919.064
106.587 | 129.758 | 132.406 | 2962920.007
133.094 | 162.027 | 165.334 | 3699761.228
148.699 | 181.025 | 184.719 | 4133558.342
154.767 | 188.413 | 192.258 | 4302252.863
150.096 | 182.726 | 186.455 | 4172398.633
139.225 | 169.491 | 172.95 | 3870193.153
118.996 | 144.865 | 147.821 | 3307872.423
88.41 | 107.63 | 109.827 | 2457644.131
44.716 | 54.437 | 55.548 | 1243024.64
10.349 | 12.599 | 12.856 | 287686.155
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
7.932 | 9.656 | 9.853 | 220488.967
63.936 | 77.835 | 79.423 | 1777298.649
106.251 | 129.349 | 131.988 | 2953577.681
133.365 | 162.358 | 165.671 | 3707309.132
149.478 | 181.973 | 185.687 | 4155210.235
154.858 | 188.522 | 192.37 | 4304756.516
150.465 | 183.175 | 186.913 | 4182651.854
139 | 169.218 | 172.671 | 3863951.737
118.091 | 143.763 | 146.697 | 3282712.94
87.467 | 106.482 | 108.655 | 2431427.966
47.648 | 58.006 | 59.19 | 1324523.098
11.192 | 13.625 | 13.903 | 311115.969
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.267 | 10.064 | 10.27 | 229807.167
54.556 | 66.417 | 67.772 | 1516570.672
103.495 | 125.994 | 128.566 | 2876974.555
138.056 | 168.068 | 171.498 | 3837699.438
153.538 | 186.915 | 190.73 | 4268061.34
160.36 | 195.221 | 199.205 | 4457713.883
158.237 | 192.637 | 196.568 | 4398705.835
145.214 | 176.782 | 180.39 | 4036677.916
122.589 | 149.239 | 152.285 | 3407752.982
91.106 | 110.912 | 113.175 | 2532582.231
50.821 | 61.869 | 63.132 | 1412730.943
13.188 | 16.055 | 16.383 | 366604.309
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.556 | 10.416 | 10.628 | 237838.512
65.058 | 79.201 | 80.818 | 1808494.532
105.722 | 128.705 | 131.331 | 2938873.083
132.494 | 161.297 | 164.589 | 3683089.053
147.718 | 179.831 | 183.501 | 4106294.261
153.353 | 186.691 | 190.501 | 4262936.866
151.507 | 184.444 | 188.208 | 4211625.861
140.01 | 170.447 | 173.925 | 3892018.201
119.558 | 145.548 | 148.519 | 3323480.291
87.725 | 106.795 | 108.975 | 2438584.66
47.083 | 57.318 | 58.488 | 1308814.453
10.801 | 13.148 | 13.417 | 300233.63
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.505 | 10.354 | 10.565 | 236423.402
66.368 | 80.796 | 82.445 | 1844911.283
109.145 | 132.873 | 135.584 | 3034040.231
138.16 | 168.195 | 171.628 | 3840598.684
152.623 | 185.802 | 189.593 | 4242635.44
158.072 | 192.436 | 196.363 | 4394117.437
153.771 | 187.2 | 191.02 | 4274556.945
141.142 | 171.825 | 175.331 | 3923483.743
119.388 | 145.342 | 148.309 | 3318771.263
88.374 | 107.585 | 109.781 | 2456623.693
46.583 | 56.709 | 57.867 | 1294912.238
11.105 | 13.519 | 13.795 | 308696.812
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.309 | 1.594 | 1.627 | 36397.008
57.68 | 70.219 | 71.652 | 1603395.268
103.645 | 126.177 | 128.752 | 2881147.507
137.27 | 167.111 | 170.522 | 3815850.264
155.905 | 189.798 | 193.671 | 4333879.552
157.862 | 192.18 | 196.102 | 4388275.076
152.43 | 185.567 | 189.354 | 4237273.168
138.682 | 168.83 | 172.275 | 3855097.235
114.209 | 139.037 | 141.875 | 3174801.036
84.924 | 103.386 | 105.496 | 2360735.196
44.989 | 54.769 | 55.887 | 1250608.788
12.059 | 14.68 | 14.98 | 335211.145
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.19 | 1.448 | 1.478 | 33070.308
52.691 | 64.145 | 65.454 | 1464702.927
105.006 | 127.834 | 130.443 | 2918983.751
130.93 | 159.393 | 162.645 | 3639607.729
144.829 | 176.314 | 179.912 | 4025985.123
149.433 | 181.919 | 185.631 | 4153968.28
145.878 | 177.59 | 181.215 | 4055132.395
132.228 | 160.973 | 164.258 | 3675690.178
111.855 | 136.172 | 138.951 | 3109374.034
82.713 | 100.694 | 102.749 | 2299267.474
45.257 | 55.096 | 56.22 | 1258067.923
10.692 | 13.016 | 13.282 | 297213.754
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.351 | 0.428 | 0.436 | 9765.397
61.942 | 75.407 | 76.946 | 1721862.944
102.255 | 124.485 | 127.025 | 2842508.88
128.602 | 156.559 | 159.754 | 3574898.724
142.567 | 173.559 | 177.101 | 3963085.9
146.528 | 178.382 | 182.023 | 4073211.945
142.755 | 173.789 | 177.335 | 3968327.542
130.018 | 158.283 | 161.514 | 3614267.356
110.008 | 133.923 | 136.656 | 3058022.512
81.799 | 99.581 | 101.614 | 2273858.075
43.439 | 52.882 | 53.962 | 1207523.167
9.959 | 12.124 | 12.372 | 276844.333
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.491 | 0.597 | 0.61 | 13640.291
61.903 | 75.361 | 76.899 | 1720802.91
102.965 | 125.349 | 127.907 | 2862241.448
128.881 | 156.899 | 160.101 | 3582660.41
143.497 | 174.692 | 178.257 | 3988951.262
148.24 | 180.466 | 184.149 | 4120797.195
144.436 | 175.836 | 179.424 | 4015066.54
132.133 | 160.858 | 164.141 | 3673061.622
111.687 | 135.967 | 138.741 | 3104692.484
81.594 | 99.331 | 101.359 | 2268152.735
43.431 | 52.873 | 53.952 | 1207309.385
10.316 | 12.559 | 12.815 | 286770.877
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.45 | 0.548 | 0.559 | 12511.231
61.381 | 74.724 | 76.249 | 1706267.194
105.778 | 128.773 | 131.401 | 2940429.597
132.686 | 161.531 | 164.827 | 3688427.199
148.989 | 181.378 | 185.079 | 4141618.196
153.429 | 186.783 | 190.595 | 4265041.464
148.907 | 181.279 | 184.978 | 4139352.451
136.664 | 166.374 | 169.769 | 3799012.559
116.068 | 141.3 | 144.183 | 3226470.469
85.645 | 104.264 | 106.391 | 2380777.94
43.783 | 53.301 | 54.389 | 1217086.9
10.621 | 12.93 | 13.194 | 295246.177
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.454 | 0.553 | 0.565 | 12628.509
53.975 | 65.709 | 67.05 | 1500410.447
101.491 | 123.554 | 126.076 | 2821260.425
136.293 | 165.921 | 169.308 | 3788682.687
154.134 | 187.641 | 191.471 | 4284637.011
159.073 | 193.654 | 197.606 | 4421933.985
155.313 | 189.077 | 192.936 | 4317421.159
141.329 | 172.053 | 175.564 | 3928689.251
117.957 | 143.6 | 146.531 | 3278991.568
82.758 | 100.749 | 102.805 | 2300521.437
42.418 | 51.639 | 52.693 | 1179137.761
11.557 | 14.07 | 14.357 | 321272.686
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.264 | 0.322 | 0.328 | 7346.24
50.34 | 61.284 | 62.534 | 1399364.694
95.921 | 116.773 | 119.156 | 2666419.867
129.176 | 157.258 | 160.467 | 3590857.285
148.366 | 180.62 | 184.306 | 4124309.168
152.205 | 185.293 | 189.075 | 4231019.744
147.575 | 179.657 | 183.323 | 4102318.59
134.04 | 163.179 | 166.509 | 3726061.779
113.285 | 137.913 | 140.727 | 3149125.22
81.266 | 98.933 | 100.952 | 2259052.59
41.096 | 50.03 | 51.051 | 1142394.333
10.714 | 13.043 | 13.309 | 297826.481
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
3.068 | 3.735 | 3.811 | 85284.473
44.885 | 54.643 | 55.758 | 1247725.933
97.657 | 118.887 | 121.313 | 2714686.87
131.055 | 159.546 | 162.802 | 3643099.959
145.754 | 177.439 | 181.061 | 4051685.065
149.527 | 182.033 | 185.748 | 4156577.093
144.738 | 176.202 | 179.798 | 4023436.68
131.467 | 160.046 | 163.313 | 3654530.492
112.455 | 136.901 | 139.695 | 3126029.818
81.527 | 99.25 | 101.276 | 2266298.053
40.467 | 49.264 | 50.269 | 1124903.384
9.922 | 12.079 | 12.326 | 275816.16
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.741 | 2.119 | 2.162 | 48387.633
50.097 | 60.988 | 62.232 | 1392607.055
98.371 | 119.757 | 122.201 | 2734548.724
132.534 | 161.345 | 164.638 | 3684189.604
146.03 | 177.776 | 181.404 | 4059369.99
150.743 | 183.514 | 187.259 | 4190389.414
146.187 | 177.967 | 181.599 | 4063732.598
133.896 | 163.004 | 166.33 | 3722061.982
113.244 | 137.862 | 140.676 | 3147972.144
83.531 | 101.69 | 103.766 | 2322012.183
41.638 | 50.69 | 51.725 | 1157466.125
10.161 | 12.37 | 12.623 | 282460.904
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.817 | 0.995 | 1.015 | 22716.2
53.239 | 64.812 | 66.135 | 1479935.866
99.987 | 121.723 | 124.208 | 2779452.893
129.429 | 157.566 | 160.781 | 3597888.966
142.884 | 173.946 | 177.496 | 3971916.276
147.911 | 180.065 | 183.74 | 4111644.525
144.025 | 175.334 | 178.913 | 4003619.726
132.661 | 161.501 | 164.797 | 3687742.094
112.82 | 137.346 | 140.149 | 3136186.535
82.839 | 100.848 | 102.906 | 2302779.447
41.547 | 50.58 | 51.612 | 1154946.081
10.489 | 12.77 | 13.03 | 291585.065
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
56.299 | 68.538 | 69.937 | 1565010.94
104.66 | 127.413 | 130.013 | 2909367.383
135.453 | 164.9 | 168.265 | 3765353.65
149.891 | 182.475 | 186.199 | 4166676.902
155.205 | 188.945 | 192.801 | 4314409.018
151.836 | 184.843 | 188.616 | 4220750.132
139.455 | 169.772 | 173.236 | 3876599.989
117.449 | 142.981 | 145.899 | 3264859.18
84.173 | 102.471 | 104.562 | 2339845.169
42.038 | 51.177 | 52.222 | 1168586.372
10.534 | 12.824 | 13.086 | 292827.02
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.271 | 0.33 | 0.337 | 7535.896
61.097 | 74.378 | 75.896 | 1698368.487
108.548 | 132.145 | 134.842 | 3017428.426
137.077 | 166.876 | 170.282 | 3810483.609
151.99 | 185.031 | 188.807 | 4225035.979
156.814 | 190.904 | 194.8 | 4359139.922
152.372 | 185.497 | 189.282 | 4235668.402
140.036 | 170.478 | 173.958 | 3892736.198
117.892 | 143.521 | 146.45 | 3277185.138
83.842 | 102.069 | 104.152 | 2330660.638
41.255 | 50.223 | 51.248 | 1146805.193
10.537 | 12.828 | 13.09 | 292915.789
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.468 | 0.57 | 0.582 | 13015.446
53.637 | 65.297 | 66.63 | 1491007.861
105.268 | 128.153 | 130.768 | 2926265.348
135.563 | 165.033 | 168.401 | 3768397.652
149.441 | 181.928 | 185.64 | 4154177.679
154.635 | 188.251 | 192.093 | 4298563.352
150.673 | 183.428 | 187.172 | 4188433.955
137.991 | 167.989 | 171.418 | 3835897.391
102.404 | 124.666 | 127.21 | 2846645.698
77.688 | 94.576 | 96.507 | 2159575.469
38.661 | 47.066 | 48.026 | 1074709.321
9.575 | 11.656 | 11.894 | 266159.275
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.093 | 0.113 | 0.115 | 2580.304
57.282 | 69.735 | 71.158 | 1592339.664
107.201 | 130.505 | 133.169 | 2979983.502
139.955 | 170.38 | 173.857 | 3890490.196
156.209 | 190.168 | 194.049 | 4342330.726
162.565 | 197.905 | 201.944 | 4519004.067
159.077 | 193.658 | 197.611 | 4422034.872
146.372 | 178.192 | 181.828 | 4068869.08
118.478 | 144.234 | 147.178 | 3293470.376
85.486 | 104.07 | 106.194 | 2376355.072
42.429 | 51.653 | 52.707 | 1179452.32
11.094 | 13.506 | 13.781 | 308394.261
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
54.281 | 66.082 | 67.43 | 1508921.881
104.624 | 127.368 | 129.967 | 2908346.945
137.405 | 167.275 | 170.689 | 3819595.762
158.978 | 193.538 | 197.488 | 4419289.038
169.607 | 206.478 | 210.692 | 4714761.005
165.727 | 201.755 | 205.872 | 4606909.361
150.54 | 183.266 | 187.006 | 4184732.326
121.936 | 148.443 | 151.473 | 3389584.663
87.837 | 106.932 | 109.114 | 2441705.313
44.288 | 53.916 | 55.016 | 1231126.136
11.289 | 13.743 | 14.024 | 313813.551
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.052 | 1.28 | 1.306 | 29231.658
54.359 | 66.177 | 67.527 | 1511091.122
104.222 | 126.879 | 129.468 | 2897178.446
138.963 | 169.173 | 172.625 | 3862923.564
151.138 | 183.994 | 187.749 | 4201356.249
154.518 | 188.109 | 191.948 | 4295317.686
150.705 | 183.467 | 187.211 | 4189320.724
137.213 | 167.041 | 170.45 | 3814253.233
114.011 | 138.795 | 141.628 | 3169280.969
79.99 | 97.379 | 99.366 | 2223570.86
38.804 | 47.239 | 48.203 | 1078668.601
8.561 | 10.422 | 10.635 | 237979.916
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
2.002 | 2.437 | 2.487 | 55649.487
51.823 | 63.088 | 64.376 | 1440571.617
105.366 | 128.272 | 130.89 | 2928987.056
134.565 | 163.818 | 167.161 | 3740653.482
150.09 | 182.718 | 186.447 | 4172221.095
155.222 | 188.966 | 192.823 | 4314889.107
149.883 | 182.466 | 186.19 | 4166467.503
135.398 | 164.832 | 168.196 | 3763809.254
113.142 | 137.739 | 140.55 | 3145153.932
80.467 | 97.959 | 99.958 | 2236819.831
38.573 | 46.959 | 47.917 | 1072266.038
8.775 | 10.682 | 10.901 | 243923.164
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
3.708 | 4.514 | 4.606 | 103073.59
25.483 | 31.022 | 31.655 | 708367.046
99.631 | 121.29 | 123.765 | 2769558.1
141.477 | 172.233 | 175.748 | 3932801.943
157.956 | 192.294 | 196.218 | 4390879.506
162.926 | 198.345 | 202.393 | 4529047.889
156.709 | 190.776 | 194.669 | 4356216.55
141.566 | 172.341 | 175.859 | 3935273.735
117.266 | 142.758 | 145.672 | 3259770.95
84.354 | 102.692 | 104.788 | 2344889.53
40.084 | 48.798 | 49.794 | 1114263.226
9.426 | 11.476 | 11.71 | 262038.848
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.425 | 1.735 | 1.77 | 39614.165
62.981 | 76.673 | 78.237 | 1750760.19
108.088 | 131.585 | 134.271 | 3004643.153
137.309 | 167.158 | 170.57 | 3816926.689
151.219 | 184.093 | 187.85 | 4203614.259
157.37 | 191.581 | 195.491 | 4374598.651
152.447 | 185.588 | 189.375 | 4237748.874
138.982 | 169.195 | 172.648 | 3863435.514
115.016 | 140.019 | 142.877 | 3197226.803
81.968 | 99.787 | 101.823 | 2278554.985
39.233 | 47.762 | 48.737 | 1090607.622
8.581 | 10.446 | 10.659 | 238528
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.675 | 0.822 | 0.839 | 18769.038
61.082 | 74.361 | 75.878 | 1697969.432
108.304 | 131.849 | 134.54 | 3010663.052
138.155 | 168.188 | 171.621 | 3840445.272
152.189 | 185.274 | 189.055 | 4230580.172
156.889 | 190.995 | 194.893 | 4361220.394
152.628 | 185.808 | 189.6 | 4242776.844
136.867 | 166.621 | 170.021 | 3804653.256
113.952 | 138.725 | 141.556 | 3167668.468
80.684 | 98.225 | 100.229 | 2242880.247
37.604 | 45.779 | 46.713 | 1045324.251
8.354 | 10.17 | 10.377 | 232221.941
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.675 | 0.822 | 0.838 | 18764.655
62.943 | 76.626 | 78.19 | 1749695.883
106.796 | 130.013 | 132.666 | 2968738.242
136.71 | 166.43 | 169.826 | 3800290.648
151.032 | 183.866 | 187.618 | 4198425.142
155.248 | 188.997 | 192.854 | 4315598.338
149.132 | 181.552 | 185.257 | 4145593.867
136.75 | 166.478 | 169.876 | 3801395.582
112.71 | 137.212 | 140.012 | 3133126.142
80.071 | 97.477 | 99.467 | 2225816.862
36.931 | 44.959 | 45.877 | 1026607.848
8.317 | 10.125 | 10.332 | 231198.151
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
46.107 | 56.13 | 57.276 | 1281687.393
96.699 | 117.72 | 120.123 | 2688047.634
132.703 | 161.551 | 164.848 | 3688890.897
153.806 | 187.242 | 191.064 | 4275524.858
159.077 | 193.659 | 197.611 | 4422046.88
154.708 | 188.34 | 192.184 | 4300595.572
139.296 | 169.578 | 173.039 | 3872177.121
112.984 | 137.546 | 140.353 | 3140750.807
76.525 | 93.16 | 95.062 | 2127242.901
35.324 | 43.003 | 43.88 | 981937.204
8.813 | 10.728 | 10.947 | 244971.08
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
44.777 | 54.511 | 55.624 | 1244718.175
90.824 | 110.569 | 112.825 | 2524748.167
128.763 | 156.754 | 159.953 | 3579357.836
144.404 | 175.796 | 179.383 | 4014158.997
153.181 | 186.481 | 190.287 | 4258146.804
142.578 | 173.573 | 177.116 | 3963404.842
120.341 | 146.502 | 149.492 | 3345257.087
120.777 | 147.033 | 150.034 | 3357381.381
76.136 | 92.687 | 94.579 | 2116437.213
35.471 | 43.182 | 44.063 | 986025.77
8.904 | 10.84 | 11.061 | 247519.523
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
48.914 | 59.547 | 60.763 | 1359714.395
99.804 | 121.5 | 123.98 | 2774360.28
135.56 | 165.029 | 168.397 | 3768308.883
155.285 | 189.042 | 192.901 | 4316630.894
160.921 | 195.904 | 199.902 | 4473309.633
155.866 | 189.75 | 193.622 | 4332786.736
141.918 | 172.77 | 176.296 | 3945063.258
117.472 | 143.009 | 145.928 | 3265500.416
80.423 | 97.906 | 99.904 | 2235606.385
36.333 | 44.231 | 45.134 | 1009983.925
8.468 | 10.309 | 10.52 | 235399.612
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
55.247 | 67.258 | 68.63 | 1535774.899
105.839 | 128.848 | 131.477 | 2942135.14
138.929 | 169.132 | 172.583 | 3861984.16
155.003 | 188.7 | 192.551 | 4308808.838
159.815 | 194.558 | 198.528 | 4442569.713
154.008 | 187.488 | 191.314 | 4281137.046
138.346 | 168.421 | 171.858 | 3845759.292
113.796 | 138.534 | 141.361 | 3163313.595
78.511 | 95.578 | 97.529 | 2182452.816
34.243 | 41.687 | 42.538 | 951891.155
7.113 | 8.659 | 8.836 | 197724.515
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
55.009 | 66.968 | 68.335 | 1529158.664
105.565 | 128.514 | 131.136 | 2934510.475
136.093 | 165.679 | 169.06 | 3783142.767
153.001 | 186.262 | 190.063 | 4253142.96
157.345 | 191.55 | 195.459 | 4373892.772
151.521 | 184.46 | 188.225 | 4212000.79
136.727 | 166.45 | 169.847 | 3800754.346
112.025 | 136.378 | 139.162 | 3114087.445
78.497 | 95.561 | 97.511 | 2182061.496
33.984 | 41.372 | 42.217 | 944698.327
6.974 | 8.49 | 8.663 | 193861.739
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
51.577 | 62.79 | 64.071 | 1433753.608
107.474 | 130.838 | 133.508 | 2987579.658
137.151 | 166.966 | 170.373 | 3812535.572
152.715 | 185.914 | 189.708 | 4245196.001
157.561 | 191.813 | 195.728 | 4379900.663
152.939 | 186.186 | 189.986 | 4251413.291
137.061 | 166.857 | 170.262 | 3810044.037
112.232 | 136.63 | 139.418 | 3119836.654
75.75 | 92.218 | 94.1 | 2105720.294
32.45 | 39.505 | 40.311 | 902059.903
6.652 | 8.098 | 8.264 | 184915.116
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
47.85 | 58.252 | 59.441 | 1330139.669
99.885 | 121.599 | 124.081 | 2776618.29
135.784 | 165.302 | 168.676 | 3774542.564
150.009 | 182.62 | 186.347 | 4169979.476
153.013 | 186.276 | 190.078 | 4253469.637
147.458 | 179.514 | 183.177 | 4099056.533
132.339 | 161.108 | 164.396 | 3678774.697
108.266 | 131.802 | 134.491 | 3009589.979
63.474 | 77.273 | 78.85 | 1764465.124
25.88 | 31.506 | 32.149 | 719414.915
4.941 | 6.015 | 6.138 | 137349.609
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
33.012 | 40.188 | 41.008 | 917663.388
76.609 | 93.263 | 95.167 | 2129589.68
115.779 | 140.948 | 143.824 | 3218434.741
112.779 | 137.296 | 140.098 | 3135045.467
117.534 | 143.085 | 146.005 | 3267230.085
133.283 | 162.257 | 165.568 | 3705010.605
111.251 | 135.436 | 138.2 | 3092572.573
88.329 | 107.531 | 109.725 | 2455381.738
53.005 | 64.528 | 65.845 | 1473444.534
16.581 | 20.185 | 20.597 | 460912.166
3.304 | 4.022 | 4.104 | 91840.448
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
54.099 | 65.859 | 67.204 | 1503845.769
100.742 | 122.643 | 125.146 | 2800451.432
127.579 | 155.313 | 158.483 | 3546453.058
141.193 | 171.887 | 175.395 | 3924903.236
144.797 | 176.275 | 179.872 | 4025093.971
139.152 | 169.402 | 172.859 | 3868160.933
99.562 | 121.206 | 123.68 | 2767643.158
103.279 | 125.731 | 128.297 | 2870966.664
61.403 | 74.751 | 76.277 | 1706884.304
28.199 | 34.329 | 35.03 | 783878.387
4.646 | 5.656 | 5.771 | 129148.351
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
43.563 | 53.033 | 54.116 | 1210970.497
94.9 | 115.53 | 117.888 | 2638038.844
128.969 | 157.005 | 160.209 | 3585087.302
144.968 | 176.482 | 180.084 | 4029831.508
148.597 | 180.901 | 184.593 | 4130728.122
138.769 | 168.936 | 172.384 | 3857520.775
124.904 | 152.057 | 155.16 | 3472099.176
104.784 | 127.563 | 130.167 | 2912802.705
61.811 | 75.248 | 76.784 | 1718230.341
16.474 | 20.055 | 20.464 | 457940.542
5.04 | 6.135 | 6.261 | 140095.443
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
25.883 | 31.509 | 32.152 | 719487.293
78.81 | 95.942 | 97.9 | 2190762.586
112.192 | 136.582 | 139.369 | 3118736.103
143.365 | 174.532 | 178.094 | 3985294.533
127.056 | 154.677 | 157.833 | 3531921.615
139.831 | 170.228 | 173.703 | 3887030.858
103.822 | 126.392 | 128.971 | 2886058.199
91.207 | 111.035 | 113.301 | 2535392.708
66.828 | 81.356 | 83.017 | 1857700.939
37.829 | 46.053 | 46.993 | 1051582.058
7.324 | 8.916 | 9.098 | 203591.002
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
38.562 | 46.945 | 47.903 | 1071951.479
95.42 | 116.163 | 118.534 | 2652493.526
132.059 | 160.767 | 164.048 | 3670988.885
147.069 | 179.041 | 182.695 | 4088255.228
149.403 | 181.882 | 185.594 | 4153129.763
143.749 | 174.998 | 178.57 | 3995946.809
129.211 | 157.3 | 160.511 | 3591825.198
102.832 | 125.187 | 127.742 | 2858544.202
68.888 | 83.863 | 85.575 | 1914950.809
25.514 | 31.061 | 31.695 | 709250.463
5.208 | 6.34 | 6.47 | 144772.61
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10.281 | 12.516 | 12.772 | 285795.339
12.067 | 14.69 | 14.99 | 335436.935
41.173 | 50.123 | 51.146 | 1144523.057
125.387 | 152.645 | 155.76 | 3485525.685
121.825 | 148.309 | 151.336 | 3386516.535
123.396 | 150.221 | 153.287 | 3430178.749
107.615 | 131.01 | 133.684 | 2991507.077
47.365 | 57.662 | 58.839 | 1316664.908
17.322 | 21.087 | 21.517 | 481507.377
11.602 | 14.124 | 14.413 | 322514.641
2.572 | 3.131 | 3.195 | 71495.153
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
40.96 | 49.864 | 50.882 | 1138608.318
96.254 | 117.179 | 119.571 | 2675689.815
132.624 | 161.455 | 164.75 | 3686697.53
111.5 | 135.739 | 138.509 | 3099491.359
134.478 | 163.713 | 167.054 | 3738250.716
124.006 | 150.964 | 154.045 | 3447141.357
90.531 | 110.212 | 112.461 | 2516599.544
79.229 | 96.453 | 98.422 | 2202427.565
38.668 | 47.074 | 48.035 | 1074898.977
21.854 | 26.605 | 27.148 | 607503.214
3.654 | 4.448 | 4.539 | 101569.711
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
41.608 | 50.653 | 51.686 | 1156618.842
33.031 | 40.212 | 41.032 | 918203.737
81.453 | 99.16 | 101.183 | 2264237.324
140.489 | 171.03 | 174.521 | 3905336.198
107.751 | 131.175 | 133.852 | 2995276.701
93.556 | 113.894 | 116.218 | 2600678.306
108.536 | 132.131 | 134.828 | 3017106.132
108.936 | 132.617 | 135.324 | 3028209.988
65.367 | 79.577 | 81.201 | 1817078.344
27.329 | 33.27 | 33.949 | 759694.442
4.645 | 5.655 | 5.77 | 129124.225
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
46.586 | 56.713 | 57.87 | 1294996.624
99.505 | 121.136 | 123.608 | 2766046.127
135.791 | 165.311 | 168.685 | 3774744.228
152.35 | 185.469 | 189.254 | 4235039.284
157.221 | 191.4 | 195.306 | 4370461.833
151.815 | 184.818 | 188.59 | 4220173.539
136.92 | 166.685 | 170.087 | 3806121.001
110.212 | 134.171 | 136.91 | 3063691.718
71.184 | 86.658 | 88.427 | 1978773.045
26.94 | 32.796 | 33.465 | 748872.363
4.892 | 5.955 | 6.077 | 135982.751
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
44.421 | 54.077 | 55.181 | 1234811.374
95.225 | 115.927 | 118.292 | 2647090.627
128.651 | 156.618 | 159.815 | 3576253.574
144.167 | 175.508 | 179.09 | 4007583.279
148.855 | 181.215 | 184.913 | 4137896.824
146.66 | 178.543 | 182.186 | 4076880.682
130.642 | 159.042 | 162.288 | 3631600.51
103.132 | 125.552 | 128.114 | 2866878.098
66.544 | 81.01 | 82.664 | 1849802.232
25.535 | 31.086 | 31.72 | 709822.673
5.369 | 6.536 | 6.669 | 149243.73
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
44.799 | 54.538 | 55.651 | 1245330.902
92.263 | 112.321 | 114.613 | 2564753.652
118.796 | 144.621 | 147.573 | 3302308.487
133.639 | 162.69 | 166.011 | 3714905.398
137.793 | 167.748 | 171.172 | 3830393.715
132.201 | 160.94 | 164.225 | 3674940.43
116.901 | 142.315 | 145.219 | 3249642.632
94.92 | 115.554 | 117.913 | 2638591.311
63.42 | 77.207 | 78.782 | 1762956.862
23.126 | 28.153 | 28.728 | 642855.658
3.471 | 4.226 | 4.312 | 96493.489
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
41.955 | 51.076 | 52.119 | 1166280.11
91.998 | 111.997 | 114.283 | 2557366.895
126.652 | 154.184 | 157.331 | 3520676.465
139.556 | 169.895 | 173.362 | 3879410.466
144.286 | 175.653 | 179.238 | 4010893.588
138.141 | 168.172 | 171.604 | 3840070.343
122.62 | 149.277 | 152.324 | 3408620.008
98.476 | 119.884 | 122.331 | 2737455.705
63.092 | 76.808 | 78.375 | 1753844.709
22.615 | 27.531 | 28.093 | 628650.892
3.305 | 4.023 | 4.105 | 91864.574
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
41.154 | 50.101 | 51.123 | 1144011.107
91.059 | 110.855 | 113.117 | 2531280.016
127.435 | 155.138 | 158.304 | 3542453.261
146.605 | 178.476 | 182.119 | 4075357.06
151.135 | 183.991 | 187.746 | 4201283.871
146.497 | 178.344 | 181.983 | 4072340.536
126.058 | 153.462 | 156.594 | 3504181.828
101.156 | 123.147 | 125.66 | 2811958.616
64.036 | 77.957 | 79.548 | 1780085
23.979 | 29.191 | 29.787 | 666559.514
3.701 | 4.505 | 4.597 | 102871.926
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
31.113 | 37.876 | 38.649 | 864872.63
85.21 | 103.733 | 105.85 | 2368665.764
122.369 | 148.97 | 152.011 | 3401620.188
143.324 | 174.481 | 178.042 | 3984137.074
148.197 | 180.414 | 184.096 | 4119607.875
141.555 | 172.328 | 175.845 | 3934971.184
121.769 | 148.24 | 151.266 | 3384948.013
93.174 | 113.43 | 115.744 | 2590074.282
59.047 | 71.883 | 73.35 | 1641392.659
22.017 | 26.803 | 27.35 | 612026.969
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8 | 9.739 | 9.938 | 222384.166
23.396 | 28.482 | 29.064 | 650367.428
72.226 | 87.927 | 89.722 | 2007747.052
116.059 | 141.289 | 144.172 | 3226220.553
152.77 | 185.981 | 189.777 | 4246728.389
142.105 | 172.997 | 176.528 | 3950252.375
130.021 | 158.287 | 161.517 | 3614351.742
106.999 | 130.259 | 132.918 | 2974366.931
68.489 | 83.378 | 85.08 | 1903871.079
24.999 | 30.434 | 31.055 | 694932.802
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
45.067 | 54.864 | 55.983 | 1252773.646
93.828 | 114.225 | 116.556 | 2608238.328
127.418 | 155.118 | 158.284 | 3541993.946
127.213 | 154.868 | 158.028 | 3536284.223
146.047 | 177.797 | 181.425 | 4059845.696
117.873 | 143.497 | 146.426 | 3276644.789
93.326 | 113.614 | 115.933 | 2594287.861
84.887 | 103.34 | 105.449 | 2359690.632
64.742 | 78.816 | 80.425 | 1799704.673
23.391 | 28.476 | 29.057 | 650226.024
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
42.696 | 51.978 | 53.038 | 1186870.938
93.395 | 113.698 | 116.019 | 2596207.186
126.87 | 154.45 | 157.603 | 3526748.999
141.305 | 172.024 | 175.535 | 3928028.272
144.888 | 176.386 | 179.985 | 4027626.023
139.099 | 169.338 | 172.794 | 3866697.571
123.639 | 150.516 | 153.588 | 3436919.997
100.57 | 122.432 | 124.931 | 2795644.979
64.204 | 78.161 | 79.756 | 1784745.776
22.451 | 27.332 | 27.89 | 624103.011
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
47.908 | 58.323 | 59.513 | 1331756.443
93.164 | 113.417 | 115.732 | 2589788.232
121.529 | 147.949 | 150.968 | 3378291.151
136.211 | 165.822 | 169.206 | 3786412.559
140.758 | 171.358 | 174.855 | 3912819.459
137.757 | 167.704 | 171.126 | 3829385.285
111.311 | 135.509 | 138.274 | 3094237.599
80.567 | 98.081 | 100.083 | 2239606.182
56.866 | 69.228 | 70.641 | 1580767.837
23.305 | 28.372 | 28.951 | 647847.384
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
26.915 | 32.766 | 33.435 | 748187.258
39.689 | 48.317 | 49.304 | 1103284.383
21.83 | 26.575 | 27.118 | 606825.844
52.188 | 63.533 | 64.829 | 1450723.951
34.727 | 42.276 | 43.139 | 965341.79
51.235 | 62.373 | 63.646 | 1424238.127
67.588 | 82.282 | 83.961 | 1878836.499
48.482 | 59.021 | 60.226 | 1347702.996
35.413 | 43.111 | 43.991 | 984408.996
12.987 | 15.81 | 16.133 | 361011.864
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
27.736 | 33.765 | 34.454 | 770999.962
75.259 | 91.62 | 93.489 | 2092063.612
93.567 | 113.908 | 116.233 | 2600997.248
142.925 | 173.996 | 177.547 | 3973057.344
114.257 | 139.096 | 141.934 | 3176139.385
98.206 | 119.556 | 121.995 | 2729955.943
60.374 | 73.499 | 74.999 | 1678289.499
52.3 | 63.67 | 64.969 | 1453848.987
38.332 | 46.664 | 47.617 | 1065544.643
13.66 | 16.629 | 16.969 | 379716.259
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
26.477 | 32.233 | 32.891 | 736014.712
77.98 | 94.933 | 96.87 | 2167711.974
118.064 | 143.731 | 146.664 | 3281975.2
147.538 | 179.611 | 183.277 | 4101278.409
138.617 | 168.751 | 172.195 | 3853295.188
130.615 | 159.01 | 162.255 | 3630862.77
128.711 | 156.692 | 159.89 | 3577934.991
62.893 | 76.566 | 78.128 | 1748316.907
61.689 | 75.1 | 76.632 | 1714843.271
20.478 | 24.93 | 25.439 | 569255.907
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
31.477 | 38.32 | 39.102 | 875005.221
67.483 | 82.153 | 83.83 | 1875901.119
16.927 | 20.607 | 21.028 | 470544.925
82.568 | 100.518 | 102.569 | 2295243.551
68.977 | 83.972 | 85.685 | 1917430.226
36.673 | 44.645 | 45.556 | 1019434.763
101.595 | 123.681 | 126.206 | 2824159.671
37.708 | 45.906 | 46.842 | 1048219.114
58.893 | 71.696 | 73.159 | 1637118.82
28.158 | 34.279 | 34.979 | 782737.319
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
21.184 | 25.789 | 26.315 | 588871.197
96.625 | 117.63 | 120.031 | 2685991.288
101.402 | 123.446 | 125.965 | 2818788.633
138.053 | 168.065 | 171.495 | 3837627.06
101.62 | 123.711 | 126.235 | 2824840.393
138.65 | 168.792 | 172.236 | 3854222.474
123.406 | 150.233 | 153.299 | 3430452.791
88.46 | 107.69 | 109.888 | 2459018.724
24.296 | 29.577 | 30.181 | 675373.499
12.981 | 15.802 | 16.125 | 360834.326
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
39.253 | 47.786 | 48.762 | 1091160.089
92.082 | 112.1 | 114.387 | 2559709.291
121.295 | 147.663 | 150.677 | 3371771.42
135.997 | 165.562 | 168.941 | 3780473.694
140.859 | 171.481 | 174.981 | 3915629.936
136.384 | 166.032 | 169.421 | 3791214.739
121.339 | 147.717 | 150.732 | 3373001.257
99.784 | 121.476 | 123.955 | 2773807.813
65.35 | 79.557 | 81.18 | 1816614.646
23.385 | 28.468 | 29.049 | 650048.486
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.111 | 9.875 | 10.076 | 225480.693
32.908 | 40.062 | 40.88 | 914784.916
69.13 | 84.159 | 85.876 | 1921696.33
48.016 | 58.454 | 59.647 | 1334752.193
95.094 | 115.766 | 118.129 | 2643429.625
55.908 | 68.062 | 69.451 | 1554140.609
97.032 | 118.126 | 120.536 | 2697308.816
94.832 | 115.447 | 117.803 | 2636143.645
48.86 | 59.482 | 60.695 | 1358218.141
21.961 | 26.736 | 27.281 | 610486.846
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
44.249 | 53.868 | 54.968 | 1230037.703
76.61 | 93.265 | 95.168 | 2129625.814
121.741 | 148.206 | 151.231 | 3384169.756
143.118 | 174.231 | 177.787 | 3978423.999
81.79 | 99.57 | 101.602 | 2273603.776
88.337 | 107.54 | 109.735 | 2455595.52
62.915 | 76.592 | 78.155 | 1748917.626
104.376 | 127.066 | 129.659 | 2901452.285
72.224 | 87.925 | 89.719 | 2007694.417
21.949 | 26.721 | 27.266 | 610148.161
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
38.165 | 46.462 | 47.41 | 1060920.001
86.624 | 105.456 | 107.608 | 2407998.152
122.695 | 149.367 | 152.416 | 3410684.089
144.106 | 175.434 | 179.014 | 4005889.744
147.743 | 179.861 | 183.531 | 4106979.366
148.396 | 180.655 | 184.342 | 4125119.286
131.381 | 159.942 | 163.206 | 3652147.469
91.41 | 111.281 | 113.552 | 2541017.014
42.52 | 51.763 | 52.819 | 1181967.981
21.619 | 26.319 | 26.856 | 600971.365
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
34.077 | 41.485 | 42.332 | 947278.631
88.488 | 107.725 | 109.923 | 2459808.989
128.304 | 156.196 | 159.384 | 3566613.08
145.426 | 177.04 | 180.654 | 4042572.912
148.638 | 180.951 | 184.643 | 4131864.807
144.639 | 176.082 | 179.675 | 4020690.846
128.633 | 156.596 | 159.792 | 3575749.359
103.239 | 125.682 | 128.247 | 2869849.722
65.324 | 79.525 | 81.148 | 1815889.024
22.84 | 27.805 | 28.372 | 634904.316
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
26.553 | 32.325 | 32.985 | 738119.31
81.947 | 99.762 | 101.797 | 2277978.392
121.304 | 147.674 | 150.688 | 3372021.336
143.814 | 175.078 | 178.651 | 3997765.247
152.678 | 185.869 | 189.662 | 4244167.828
148.276 | 180.51 | 184.194 | 4121801.242
132.14 | 160.866 | 164.149 | 3673246.895
103.145 | 125.568 | 128.131 | 2867245.292
63.626 | 77.458 | 79.039 | 1768690.711
25.58 | 31.141 | 31.776 | 711076.636
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
30.598 | 37.25 | 38.01 | 850571.36
84.711 | 103.126 | 105.231 | 2354804.066
124.427 | 151.477 | 154.568 | 3458850.205
143.284 | 174.432 | 177.992 | 3983020.132
148.205 | 180.423 | 184.105 | 4119817.274
141.686 | 172.488 | 176.008 | 3938620.178
125.813 | 153.164 | 156.289 | 3497371.554
99.935 | 121.659 | 124.142 | 2777992.883
61.747 | 75.171 | 76.705 | 1716464.428
22.48 | 27.367 | 27.926 | 624905.394
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
24.929 | 30.349 | 30.968 | 692989.351
86.388 | 105.167 | 107.314 | 2401413.778
70.704 | 86.074 | 87.831 | 1965435.305
136.976 | 166.754 | 170.157 | 3807689.523
138.711 | 168.865 | 172.312 | 3855904.001
131.733 | 160.37 | 163.643 | 3661924.984
118.596 | 144.378 | 147.324 | 3296752.176
95.54 | 116.31 | 118.683 | 2655839.969
58.131 | 70.769 | 72.213 | 1615947.016
21.916 | 26.681 | 27.225 | 609232.883
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
31.333 | 38.144 | 38.923 | 870993.416
81.682 | 99.439 | 101.469 | 2270612.409
119.498 | 145.476 | 148.445 | 3321827.273
138.991 | 169.206 | 172.659 | 3863685.43
143.654 | 174.884 | 178.453 | 3993330.261
138.556 | 168.677 | 172.119 | 3851601.653
123.573 | 150.436 | 153.506 | 3435089.441
96.615 | 117.618 | 120.018 | 2685712.863
60.337 | 73.454 | 74.953 | 1677261.326
22.066 | 26.863 | 27.411 | 613393.827
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
33.042 | 40.226 | 41.047 | 918522.679
87.496 | 106.517 | 108.691 | 2432230.349
124.116 | 151.098 | 154.182 | 3450201.75
143.055 | 174.154 | 177.708 | 3976665.821
148.934 | 181.311 | 185.011 | 4140090.191
141.976 | 172.84 | 176.368 | 3946668.024
125.737 | 153.071 | 156.195 | 3495254.948
100.45 | 122.288 | 124.783 | 2792338.943
61.049 | 74.32 | 75.837 | 1697042.146
22.892 | 27.869 | 28.438 | 636364.326
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.46 | 13.952 | 14.237 | 318579.487
55.329 | 67.357 | 68.731 | 1538040.644
86.482 | 105.283 | 107.431 | 2404046.607
138.294 | 168.358 | 171.794 | 3844320.056
143.618 | 174.839 | 178.408 | 3992314.206
133.434 | 162.442 | 165.757 | 3709228.457
118.27 | 143.981 | 146.92 | 3287692.658
90.939 | 110.709 | 112.968 | 2527945.581
63.667 | 77.507 | 79.089 | 1769815.388
20.883 | 25.423 | 25.942 | 580513.175
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
5.284 | 6.433 | 6.564 | 146889.216
18.412 | 22.415 | 22.872 | 511824.116
53.613 | 65.268 | 66.6 | 1490342.499
108.231 | 131.759 | 134.448 | 3008614.441
104.005 | 126.614 | 129.198 | 2891134.421
76.605 | 93.259 | 95.162 | 2129488.793
76.804 | 93.501 | 95.409 | 2135016.595
68.101 | 82.906 | 84.598 | 1893089.517
48.002 | 58.437 | 59.63 | 1334365.256
18.011 | 21.926 | 22.374 | 500667.735
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
23.128 | 28.156 | 28.731 | 642920.301
79.602 | 96.907 | 98.885 | 2212793.681
113.261 | 137.883 | 140.697 | 3148447.85
69.166 | 84.202 | 85.92 | 1922683.986
56.659 | 68.976 | 70.384 | 1575014.245
45.524 | 55.42 | 56.551 | 1265474.533
33.787 | 41.132 | 41.972 | 939218.777
39.302 | 47.845 | 48.822 | 1092510.556
22.849 | 27.816 | 28.383 | 635154.232
10.583 | 12.883 | 13.146 | 294177.487
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
5.384 | 6.554 | 6.688 | 149659.176
68.101 | 82.906 | 84.598 | 1893089.517
108.141 | 131.65 | 134.336 | 3006118.523
71.882 | 87.508 | 89.294 | 1998178.936
94.525 | 115.074 | 117.422 | 2627620.093
132.196 | 160.934 | 164.218 | 3674799.026
107.499 | 130.869 | 133.54 | 2988285.537
107.27 | 130.589 | 133.254 | 2981898.444
68.533 | 83.432 | 85.134 | 1905096.533
24.325 | 29.613 | 30.217 | 676187.89
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
34.938 | 42.533 | 43.401 | 971208.277
86.844 | 105.723 | 107.881 | 2414102.547
126.734 | 154.285 | 157.434 | 3522974.992
141.933 | 172.789 | 176.315 | 3945490.712
148.83 | 181.184 | 184.882 | 4137195.328
140.658 | 171.236 | 174.73 | 3910033.108
88.197 | 107.37 | 109.561 | 2451708.618
62.61 | 76.221 | 77.777 | 1740446.709
34.031 | 41.43 | 42.275 | 946012.55
18.843 | 22.94 | 23.408 | 523811.389
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
2.518 | 3.065 | 3.128 | 69991.274
89.823 | 109.35 | 111.582 | 2496919.611
98.547 | 119.97 | 122.418 | 2739418.899
102.623 | 124.932 | 127.482 | 2852725.967
69.632 | 84.77 | 86.5 | 1935651.18
82.74 | 100.726 | 102.782 | 2300005.214
115.905 | 141.101 | 143.981 | 3221934.706
38.85 | 47.295 | 48.26 | 1079946.69
27.348 | 33.293 | 33.972 | 760218.4
19.238 | 23.42 | 23.898 | 534778.224
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.395 | 17.524 | 17.882 | 400150.323
86.299 | 105.06 | 107.204 | 2398958.377
130.154 | 158.448 | 161.682 | 3618036.98
146.604 | 178.475 | 182.117 | 4075328.551
149.422 | 181.905 | 185.617 | 4153653.721
145.102 | 176.646 | 180.251 | 4033569.271
129.087 | 157.149 | 160.356 | 3588373.485
102.615 | 124.922 | 127.472 | 2852500.177
66.499 | 80.956 | 82.608 | 1848560.277
25.593 | 31.156 | 31.792 | 711427.439
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
31.942 | 38.886 | 39.679 | 887927.515
89.688 | 109.185 | 111.413 | 2493153.339
123.253 | 150.047 | 153.109 | 3426203.078
140.428 | 170.956 | 174.445 | 3903642.663
145.136 | 176.687 | 180.293 | 4034508.675
142.462 | 173.432 | 176.971 | 3960178.919
130.771 | 159.2 | 162.449 | 3635201.252
98.274 | 119.638 | 122.079 | 2731834.751
53.704 | 65.379 | 66.713 | 1492874.551
22.605 | 27.519 | 28.08 | 628372.467
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
29.373 | 35.759 | 36.489 | 816525.514
76.075 | 92.613 | 94.503 | 2114743.678
108.229 | 131.757 | 134.445 | 3008561.806
124.174 | 151.168 | 154.253 | 3451802.133
79.933 | 97.309 | 99.295 | 2221978.212
20.527 | 24.989 | 25.499 | 570606.374
31.731 | 38.629 | 39.417 | 882061.028
32.759 | 39.881 | 40.694 | 910643.715
33.103 | 40.299 | 41.121 | 920195.44
13.972 | 17.01 | 17.357 | 388405.231
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.503 | 11.568 | 11.805 | 264155.564
57.034 | 69.433 | 70.85 | 1585445.004
100.556 | 122.416 | 124.914 | 2795270.05
135.92 | 165.468 | 168.845 | 3778328.579
147.202 | 179.202 | 182.859 | 4091936.083
139.81 | 170.204 | 173.678 | 3886470.656
122.35 | 148.948 | 151.988 | 3401108.238
92.591 | 112.72 | 115.02 | 2573865.805
55.554 | 67.631 | 69.011 | 1544298.451
21.463 | 26.129 | 26.663 | 596637.266
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
5.543 | 6.748 | 6.885 | 154082.044
65.079 | 79.227 | 80.844 | 1809083.133
89.937 | 109.489 | 111.723 | 2500088.516
140.309 | 170.811 | 174.297 | 3900332.354
111.145 | 135.307 | 138.069 | 3089629.458
104.186 | 126.835 | 129.423 | 2896174.399
109.79 | 133.657 | 136.385 | 3051954.361
49.685 | 60.487 | 61.721 | 1381164.514
49.189 | 59.882 | 61.104 | 1367358.803
18.187 | 22.14 | 22.592 | 505554.301
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
24.215 | 29.48 | 30.081 | 673143.888
43.91 | 53.456 | 54.547 | 1220622.999
47.386 | 57.687 | 58.865 | 1317241.501
92.079 | 112.096 | 114.384 | 2559624.905
101.189 | 123.187 | 125.701 | 2812873.894
108.241 | 131.772 | 134.461 | 3008904.874
98.136 | 119.47 | 121.908 | 2728000.484
78.287 | 95.306 | 97.251 | 2176235.526
33.98 | 41.366 | 42.211 | 944569.041
17.266 | 21.019 | 21.448 | 479955.246
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.813 | 14.381 | 14.674 | 328376.745
43.944 | 53.498 | 54.589 | 1221574.411
92.731 | 112.89 | 115.194 | 2577752.707
121.698 | 148.155 | 151.178 | 3382992.444
136.695 | 166.412 | 169.808 | 3799879.585
134.498 | 163.737 | 167.078 | 3738798.8
116.323 | 141.611 | 144.501 | 3233571.176
72.565 | 88.34 | 90.143 | 2017173.764
43.268 | 52.674 | 53.749 | 1202769.239
27.204 | 33.118 | 33.794 | 756222.986
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
21.927 | 26.694 | 27.239 | 609535.434
62.78 | 76.428 | 77.987 | 1745167.745
101.891 | 124.042 | 126.573 | 2832392.68
128.095 | 155.941 | 159.124 | 3560794.845
137.186 | 167.009 | 170.417 | 3813515.493
132.542 | 161.355 | 164.648 | 3684415.394
115.046 | 140.056 | 142.915 | 3198069.703
94.342 | 114.851 | 117.195 | 2622531.863
58.231 | 70.89 | 72.336 | 1618712.593
21.339 | 25.978 | 26.508 | 593185.553
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
11.647 | 14.179 | 14.469 | 323768.604
54.694 | 66.584 | 67.943 | 1520392.931
110.688 | 134.751 | 137.501 | 3076928.571
133.198 | 162.154 | 165.463 | 3702656.091
141.086 | 171.756 | 175.262 | 3921919.604
130.977 | 159.45 | 162.704 | 3640914.327
114.597 | 139.509 | 142.357 | 3185582.598
87.816 | 106.907 | 109.088 | 2441128.72
55.409 | 67.454 | 68.831 | 1540262.52
21.486 | 26.157 | 26.691 | 597274.119
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
4.043 | 4.922 | 5.023 | 112391.79
26.852 | 32.689 | 33.356 | 746429.08
44.761 | 54.492 | 55.604 | 1244278.603
58.421 | 71.122 | 72.573 | 1624006.87
51.216 | 62.35 | 63.622 | 1423709.786
47.228 | 57.495 | 58.668 | 1312850.384
72.012 | 87.667 | 89.456 | 2001803.804
50.46 | 61.429 | 62.683 | 1402687.121
19.02 | 23.155 | 23.627 | 528722.081
13.896 | 16.917 | 17.262 | 386284.242
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
22.483 | 27.371 | 27.93 | 624994.163
42.293 | 51.487 | 52.538 | 1175666.305
64.597 | 78.64 | 80.244 | 1795676.367
72.135 | 87.817 | 89.609 | 2005227.008
110.792 | 134.877 | 137.63 | 3079811.426
29.554 | 35.979 | 36.714 | 821553.484
34.235 | 41.677 | 42.528 | 951665.365
29.181 | 35.525 | 36.25 | 811182.985
17.28 | 21.036 | 21.466 | 480346.566
13.938 | 16.968 | 17.314 | 387449.436
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
8.112 | 9.876 | 10.077 | 225504.819
22.299 | 27.146 | 27.7 | 619861.033
44.57 | 54.259 | 55.366 | 1238960.2
61.894 | 75.35 | 76.887 | 1720548.611
52.58 | 64.011 | 65.317 | 1461634.799
50.792 | 61.834 | 63.096 | 1411928.56
72.323 | 88.046 | 89.843 | 2010456.642
50.314 | 61.252 | 62.502 | 1398639.072
26.417 | 32.16 | 32.816 | 734345.303
22.2 | 27.026 | 27.577 | 617115.199
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
5.413 | 6.59 | 6.725 | 150477.95
52.782 | 64.256 | 65.567 | 1467234.979
60.562 | 73.728 | 75.232 | 1683514.75
80.984 | 98.59 | 100.602 | 2251218.526
46.753 | 56.916 | 58.078 | 1299637.657
49.11 | 59.786 | 61.006 | 1365165.436
99.8 | 121.496 | 123.975 | 2774259.393
63.404 | 77.188 | 78.763 | 1762521.673
33.56 | 40.856 | 41.69 | 932912.718
12.603 | 15.343 | 15.656 | 350343.197
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
20.814 | 25.339 | 25.856 | 578593.85
50.117 | 61.011 | 62.257 | 1393147.514
65.402 | 79.62 | 81.245 | 1818058.265
75.353 | 91.734 | 93.606 | 2094672.425
61.317 | 74.647 | 76.17 | 1704501.281
43.512 | 52.971 | 54.052 | 1209551.004
71.728 | 87.321 | 89.103 | 1993905.097
49.134 | 59.816 | 61.036 | 1365842.806
30.148 | 36.701 | 37.45 | 838043.738
21.048 | 25.624 | 26.147 | 585101.573
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
3.167 | 3.856 | 3.935 | 88046.698
44.365 | 54.009 | 55.112 | 1233259.243
81.519 | 99.241 | 101.266 | 2266084.271
75.194 | 91.54 | 93.408 | 2090245.174
50.331 | 61.272 | 62.523 | 1399102.77
53.363 | 64.963 | 66.289 | 1483383.196
51.297 | 62.449 | 63.723 | 1425967.796
48.263 | 58.755 | 59.954 | 1341622.727
38.18 | 46.48 | 47.428 | 1061331.064
21.771 | 26.504 | 27.045 | 605196.952
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
17.886 | 21.774 | 22.218 | 497191.896
70.158 | 85.41 | 87.153 | 1950267.009
113.714 | 138.435 | 141.26 | 3161047.85
139.661 | 170.022 | 173.491 | 3882313.064
145.44 | 177.057 | 180.671 | 4042959.849
140.921 | 171.555 | 175.057 | 3917331.206
127.341 | 155.024 | 158.188 | 3539848.831
96.943 | 118.017 | 120.426 | 2694829.399
56.366 | 68.62 | 70.02 | 1566877.63
20.92 | 25.467 | 25.987 | 581524.957
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
10 | 12.174 | 12.423 | 277985.401
46.149 | 56.181 | 57.328 | 1282852.587
96.084 | 116.972 | 119.359 | 2670960.013
116.165 | 141.418 | 144.304 | 3229168.051
137.19 | 167.014 | 170.422 | 3813628.388
136.566 | 166.255 | 169.648 | 3796295.234
113.911 | 138.674 | 141.504 | 3166511.009
79.649 | 96.964 | 98.943 | 2214095.896
46.09 | 56.11 | 57.255 | 1281223.695
23.506 | 28.616 | 29.2 | 653423.438
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.117 | 17.185 | 17.536 | 392412.763
54.468 | 66.309 | 67.662 | 1514110.998
98.922 | 120.426 | 122.884 | 2749837.65
125.729 | 153.062 | 156.185 | 3495041.166
138.368 | 168.449 | 171.886 | 3846388.41
135.806 | 165.329 | 168.703 | 3775155.291
122.128 | 148.678 | 151.712 | 3394939.2
95.155 | 115.841 | 118.205 | 2645135.168
50.16 | 61.064 | 62.31 | 1394348.842
18.402 | 22.402 | 22.859 | 511533.683
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
14.113 | 17.182 | 17.532 | 392328.267
35.117 | 42.751 | 43.624 | 976187.995
63.281 | 77.038 | 78.61 | 1759098.469
80.356 | 97.825 | 99.822 | 2233756.086
98.1 | 119.426 | 121.864 | 2727000.82
109.786 | 133.653 | 136.381 | 3051857.857
106.096 | 129.16 | 131.796 | 2949267.708
86.297 | 105.057 | 107.201 | 2398893.734
38.232 | 46.544 | 47.494 | 1062791.074
12.835 | 15.626 | 15.945 | 356802.668
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.091 | 15.937 | 16.262 | 363906.727
6.541 | 7.963 | 8.125 | 181826.214
15.487 | 18.853 | 19.238 | 430498.923
26.136 | 31.818 | 32.467 | 726535.365
33.578 | 40.877 | 41.712 | 933400.542
63.4 | 77.182 | 78.757 | 1762392.387
42.664 | 51.938 | 52.998 | 1185967.778
39.441 | 48.015 | 48.995 | 1096385.34
27.266 | 33.193 | 33.87 | 757936.264
11.581 | 14.099 | 14.387 | 321938.048
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.078 | 1.312 | 1.339 | 29961.663
50.571 | 61.565 | 62.821 | 1405783.648
112.271 | 136.678 | 139.467 | 3120929.47
117.768 | 143.369 | 146.295 | 3273721.417
136.238 | 165.855 | 169.24 | 3787166.69
113.859 | 138.611 | 141.439 | 3165067.39
91.008 | 110.792 | 113.053 | 2529848.515
57.094 | 69.506 | 70.925 | 1587114.413
31.327 | 38.137 | 38.916 | 870832.269
18.124 | 22.063 | 22.514 | 503800.506
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
1.279 | 1.557 | 1.589 | 35554.108
69.295 | 84.359 | 86.08 | 1926268.337
110.642 | 134.694 | 137.443 | 3075634.091
131.348 | 159.902 | 163.166 | 3651236.574
136.405 | 166.058 | 169.447 | 3791803.34
130.322 | 158.653 | 161.891 | 3622714.147
116.032 | 141.256 | 144.139 | 3225470.805
92.618 | 112.752 | 115.054 | 2574607.928
53.334 | 64.928 | 66.253 | 1482580.813
17.886 | 21.774 | 22.219 | 497196.279
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.451 | 0.549 | 0.56 | 12535.357
57.753 | 70.308 | 71.743 | 1605427.488
100.859 | 122.785 | 125.291 | 2803697.098
130.595 | 158.985 | 162.229 | 3630293.912
131.805 | 160.458 | 163.732 | 3663928.695
70.534 | 85.868 | 87.62 | 1960721.894
72.434 | 88.181 | 89.98 | 2013536.778
35.03 | 42.645 | 43.515 | 973764.455
28.74 | 34.988 | 35.702 | 798921.67
10.956 | 13.338 | 13.611 | 304564.377
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.767 | 0.933 | 0.952 | 21308.825
45.703 | 55.639 | 56.774 | 1270466.259
103.378 | 125.851 | 128.42 | 2873712.498
137.417 | 167.291 | 170.705 | 3819950.838
105.93 | 128.958 | 131.59 | 2944655.184
135.82 | 165.347 | 168.721 | 3775558.619
86.413 | 105.199 | 107.346 | 2402131.665
61.991 | 75.467 | 77.008 | 1723234.185
34.156 | 41.582 | 42.43 | 949484.006
12.232 | 14.891 | 15.195 | 340025.333
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.774 | 0.942 | 0.961 | 21510.489
12.192 | 14.842 | 15.145 | 338908.391
13.999 | 17.042 | 17.39 | 389142.971
15.916 | 19.377 | 19.772 | 442449.952
22.878 | 27.852 | 28.42 | 635973.006
39.622 | 48.235 | 49.22 | 1101413.31
39.916 | 48.594 | 49.585 | 1109598.067
68.443 | 83.322 | 85.022 | 1902588.607
53.877 | 65.589 | 66.928 | 1497676.731
21.558 | 26.245 | 26.78 | 599277.83
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
9.059 | 11.028 | 11.253 | 251817.488
19.672 | 23.949 | 24.437 | 546849.883
33.287 | 40.523 | 41.35 | 925312.179
45.55 | 55.452 | 56.584 | 1266204.538
53.769 | 65.458 | 66.794 | 1494680.981
123.117 | 149.881 | 152.94 | 3422417.063
96.207 | 117.122 | 119.512 | 2674383.217
67.212 | 81.823 | 83.493 | 1868365.223
21.119 | 25.71 | 26.235 | 587069.15
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
50.293 | 61.226 | 62.476 | 1398050.471
63.247 | 76.996 | 78.567 | 1758142.674
79.36 | 96.612 | 98.584 | 2206060.168
103.529 | 126.035 | 128.608 | 2877913.959
105.919 | 128.945 | 131.577 | 2944357.016
56 | 68.174 | 69.566 | 1556701.17
28.34 | 34.501 | 35.205 | 787801.423
33.095 | 40.289 | 41.112 | 919974.033
10.255 | 12.484 | 12.739 | 285065.334
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
40.917 | 49.812 | 50.828 | 1137414.615
36.899 | 44.921 | 45.838 | 1025733.087
60.985 | 74.243 | 75.758 | 1695276.233
116.57 | 141.911 | 144.807 | 3240425.319
85.175 | 103.691 | 105.807 | 2367702.234
93.878 | 114.286 | 116.618 | 2609629.312
69.46 | 84.56 | 86.286 | 1930861.118
38.24 | 46.553 | 47.503 | 1063000.473
16.099 | 19.599 | 19.999 | 447526.174
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.577 | 0.703 | 0.717 | 16047.33
56.37 | 68.624 | 70.025 | 1566978.517
107.024 | 130.291 | 132.95 | 2975084.818
131.088 | 159.585 | 162.842 | 3643998.846
144.465 | 175.87 | 179.46 | 4015856.915
124.177 | 151.172 | 154.257 | 3451890.902
116.343 | 141.635 | 144.526 | 3234123.643
86.757 | 105.617 | 107.772 | 2411679.007
48.82 | 59.433 | 60.646 | 1357105.582
22.732 | 27.673 | 28.238 | 631896.558
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
59.026 | 71.858 | 73.324 | 1640816.066
102.556 | 124.851 | 127.399 | 2850871.285
132.939 | 161.838 | 165.141 | 3695446.872
135.469 | 164.919 | 168.285 | 3765793.222
137.219 | 167.05 | 170.459 | 3814447.162
105.057 | 127.896 | 130.506 | 2920398.861
93.645 | 114.003 | 116.329 | 2603162.106
49.166 | 59.854 | 61.075 | 1366717.567
20.439 | 24.883 | 25.391 | 568179.482
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.176 | 0.215 | 0.219 | 4902.957
59.014 | 71.843 | 73.309 | 1640477.381
110.762 | 134.84 | 137.592 | 3078968.526
139.92 | 170.337 | 173.813 | 3889510.275
148.343 | 180.592 | 184.277 | 4123667.932
142.758 | 173.792 | 177.339 | 3968404.303
127.581 | 155.316 | 158.485 | 3546513.318
101.449 | 123.503 | 126.024 | 2820095.231
65.15 | 79.312 | 80.931 | 1811034.319
24.697 | 30.066 | 30.68 | 686534.263
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
39.513 | 48.102 | 49.084 | 1098377.043
112.998 | 137.563 | 140.37 | 3141137.744
96.023 | 116.898 | 119.283 | 2669266.478
42.907 | 52.235 | 53.301 | 1192741.808
95.427 | 116.172 | 118.543 | 2652695.19
29.109 | 35.438 | 36.161 | 809191.282
53.776 | 65.466 | 66.802 | 1494866.254
46.173 | 56.21 | 57.358 | 1283517.949
21.166 | 25.767 | 26.293 | 588371.365
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
49.089 | 59.76 | 60.98 | 1364576.835
108.06 | 131.551 | 134.236 | 3003864.896
137.01 | 166.795 | 170.199 | 3808628.927
145.324 | 176.916 | 180.527 | 4039738.309
142.508 | 173.488 | 177.028 | 3961457.008
128.029 | 155.862 | 159.043 | 3558980.68
100.353 | 122.169 | 124.663 | 2789633.736
52.049 | 63.364 | 64.657 | 1446865.558
16.83 | 20.489 | 20.907 | 467847.343
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0.378 | 0.46 | 0.47 | 10507.52
31.105 | 37.867 | 38.639 | 864658.848
71.937 | 87.576 | 89.363 | 1999723.332
120.008 | 146.097 | 149.079 | 3336007.913
122.988 | 149.725 | 152.78 | 3418844.72
106.95 | 130.2 | 132.857 | 2973012.081
90.97 | 110.746 | 113.006 | 2528796.216
84.963 | 103.433 | 105.544 | 2361811.621
63.035 | 76.738 | 78.304 | 1752252.061
29.533 | 35.953 | 36.686 | 820956.117
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
49.143 | 59.826 | 61.047 | 1366080.714
99.852 | 121.56 | 124.04 | 2775715.02
133.372 | 162.366 | 165.68 | 3707498.788
141.8 | 172.626 | 176.149 | 3941777.075
137.963 | 167.955 | 171.382 | 3835114.751
124.483 | 151.544 | 154.637 | 3460390.328
100.139 | 121.908 | 124.396 | 2783674.097
63.819 | 77.693 | 79.278 | 1774052.983
23.861 | 29.048 | 29.641 | 663289.722
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
62.98 | 76.671 | 78.235 | 1750719.673
100.183 | 121.961 | 124.451 | 2784891.926
133.729 | 162.801 | 166.123 | 3717425.332
143.863 | 175.138 | 178.712 | 3999132.105
137.737 | 167.679 | 171.101 | 3828820.81
120.597 | 146.813 | 149.809 | 3352361.146
94.493 | 115.035 | 117.383 | 2626733.324
55.433 | 67.484 | 68.861 | 1540939.89
23.833 | 29.014 | 29.606 | 662511.465
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
44.495 | 54.168 | 55.273 | 1236879.728
91.904 | 111.883 | 114.167 | 2554762.465
140.733 | 171.327 | 174.823 | 3912113.58
146.176 | 177.953 | 181.585 | 4063418.039
140.84 | 171.457 | 174.956 | 3915085.204
126.265 | 153.714 | 156.851 | 3509935.42
83.298 | 101.407 | 103.476 | 2315540.594
44.143 | 53.739 | 54.836 | 1227090.205
14.832 | 18.057 | 18.425 | 412310.751
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
44.359 | 54.002 | 55.104 | 1233093.713
101.747 | 123.866 | 126.394 | 2828380.875
131.18 | 159.698 | 162.957 | 3646571.415
139.614 | 169.965 | 173.434 | 3881015.232
147.305 | 179.327 | 182.987 | 4094794.812
130.442 | 158.799 | 162.04 | 3626048.582
102.418 | 124.682 | 127.227 | 2847020.627
65.692 | 79.973 | 81.605 | 1826118.119
24.42 | 29.729 | 30.336 | 678837.22
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
49.273 | 59.984 | 61.209 | 1369693.574
99.137 | 120.688 | 123.151 | 2755817.032
130.207 | 158.513 | 161.748 | 3619516.733
141.842 | 172.677 | 176.201 | 3942942.269
137.916 | 167.898 | 171.324 | 3833812.536
128.072 | 155.914 | 159.096 | 3560170
102.727 | 125.059 | 127.611 | 2855620.83
53.428 | 65.043 | 66.37 | 1485201.634
20.329 | 24.748 | 25.253 | 565102.698
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
57.492 | 69.99 | 71.419 | 1598170.017
103.284 | 125.737 | 128.303 | 2871103.685
128.259 | 156.141 | 159.328 | 3565359.117
103.237 | 125.68 | 128.245 | 2869801.47
97.602 | 118.82 | 121.244 | 2713154.482
96.079 | 116.966 | 119.353 | 2670822.992
98.077 | 119.398 | 121.835 | 2726359.584
53.462 | 65.085 | 66.413 | 1486157.429
16.759 | 20.402 | 20.818 | 465863.375
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
49.763 | 60.581 | 61.818 | 1383321.747
110.645 | 134.698 | 137.447 | 3075722.86
127.16 | 154.803 | 157.962 | 3534804.47
139.959 | 170.385 | 173.862 | 3890603.091
135.757 | 165.269 | 168.642 | 3773788.433
122.564 | 149.208 | 152.253 | 3407047.103
100.331 | 122.142 | 124.635 | 2789016.626
56.611 | 68.918 | 70.325 | 1573687.904
21.82 | 26.563 | 27.106 | 606551.802
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
59.541 | 72.485 | 73.964 | 1655133.727
107.862 | 131.31 | 133.99 | 2998361.22
128.532 | 156.473 | 159.667 | 3572943.265
134.591 | 163.849 | 167.193 | 3741367.096
131.256 | 159.79 | 163.051 | 3648676.013
118.58 | 144.358 | 147.304 | 3296300.596
96.832 | 117.882 | 120.288 | 2691744.88
65.894 | 80.219 | 81.856 | 1831734.69
26.672 | 32.47 | 33.133 | 741429.619
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
60.449 | 73.59 | 75.092 | 1680369.971
104.095 | 126.724 | 129.31 | 2893642.347
128.213 | 156.085 | 159.271 | 3564081.028
136.869 | 166.623 | 170.023 | 3804701.508
134.173 | 163.342 | 166.675 | 3729775.416
121.629 | 148.07 | 151.092 | 3381061.111
100.271 | 122.07 | 124.561 | 2787363.608
63.261 | 77.014 | 78.585 | 1758546.002
26.128 | 31.808 | 32.457 | 726309.575
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
61.65 | 75.053 | 76.584 | 1713766.846
106.072 | 129.131 | 131.767 | 2948606.729
127.939 | 155.752 | 158.931 | 3556472.754
137.201 | 167.027 | 170.436 | 3813930.939
135.023 | 164.376 | 167.731 | 3753394.886
121.834 | 148.32 | 151.347 | 3386766.451
99.749 | 121.434 | 123.912 | 2772844.283
67.174 | 81.777 | 83.446 | 1867312.924
27.798 | 33.841 | 34.531 | 772729.631
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
65.279 | 79.47 | 81.092 | 1814635.061
101.067 | 123.039 | 125.55 | 2809491.207
100.924 | 122.864 | 125.371 | 2805499.145
127.868 | 155.665 | 158.842 | 3554488.786
133.747 | 162.823 | 166.146 | 3717929.547
118.082 | 143.752 | 146.686 | 3282463.024
94.32 | 114.824 | 117.167 | 2621914.753
63.047 | 76.752 | 78.319 | 1752578.738
25.303 | 30.803 | 31.432 | 703367.585
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
13.356 | 16.26 | 16.591 | 371277.093
98.664 | 120.113 | 122.564 | 2742680.956
125.264 | 152.495 | 155.607 | 3482102.481
139.107 | 169.348 | 172.804 | 3866923.361
138.609 | 168.741 | 172.185 | 3853069.398
126.327 | 153.79 | 156.928 | 3511665.089
102.486 | 124.765 | 127.311 | 2848911.443
66.173 | 80.559 | 82.203 | 1839496.376
27.719 | 33.745 | 34.434 | 770540.647
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
372205.219 | 453119.359 | 462366.748 | 10346618088.321